## Installation overview
BLECF installation (tunnel electronic) | [13 empty] | Tests
| ARC | [6 empty] | straight section | [5 empty] | otical link |  |  |  |  | HV levels test |  |  | rad.
| BLECF |  |  |  | Backplane | 220V | Completed | BLECF |  |  |  | 220V |  | connection | connection | connection | TC | CFC - |  | resistor | completely | source
| to install | installed | Rst. OK | tested | soldered | checked |  | to install | installed | Rst. OK | tested | checked | Completed | total installed | tunnel surface | Jumper |  | ID | scanned | replaced | tested | test
1 LEFT | 22 | 22 | 22 | 22 | 22 | 22 | OK | 19 | 19 | 19 | 19 | 19 | OK | 82 | 82 | 82 | 21 | 41
1 RIGHT | 23 | 23 | 23 | 23 | 23 | 23 | OK | 19 | 19 | 19 | 19 | 19 | OK | 84 | 84 | 84 | 21 | 42
2 LEFT | 22 | 22 | 22 | 22 | 22 | 22 | OK | 22 | 22 | 22 | 22 | 22 | OK | 88 | 86 +2 spares | 88 | 22 | 44
2 RIGHT | 23 | 23 | 23 | 23 | 23 | 23 | OK | 21 | 21 | 21 | 21 | 21 | OK | 88 | 88 | 88 | 22 | 44
3 LEFT | 22 | 22 | 22 | 22 | 22 | 22 | OK | 18 | 18 | 18 | 18 | 18 | OK | 80 | 80 | 80 | 20 | 40
3 RIGHT | 23 | 23 | 23 | 23 | 23 | 23 | OK | 18 | 18 | 18 | 18 | 18 | OK | 82 | 80 + 2 spares | 82 | 21 | 41
4 LEFT | 22 | 22 | 22 | 22 | 22 | 22 | OK | 8 | 8 | 8 | 8 | 8 | OK | 60 | 60 | 60 | 15 | 30
4 RIGHT | 23 | 23 | 23 | 23 | 23 | 23 | OK | 8 | 8 | 8 | 8 | 8 | OK | 62 | 62 | 62 | 14 | 31
5 LEFT | 22 | 22 | 22 | 22 | 22 | 22 | OK | 19 | 19 | 19 | 19 | 19 | OK | 82 | 81 | 82 |  | 41
5 RIGHT | 23 | 23 | 23 | 23 | 23 | 23 | OK | 19 | 19 | 19 | 19 | 19 | OK | 84 | 84 | 84 |  | 42
6 LEFT | 22 | 22 | 22 | 22 | 22 | 22 | OK | 21 | 21 | 21 | 21 | 21 | OK | 86 | 86 | 86 |  | 43
6 RIGHT | 23 | 23 | 23 | 23 | 23 | 23 | OK | 21 | 21 | 21 | 21 | 21 | OK | 88 | 88 | 88 |  | 44
7 LEFT | 22 | 22 | 22 | 22 | 22 | 22 | OK | 28 | 28 | 28 | 28 | 28 | OK | 100 | 100 | 99 |  | 50
7 RIGHT | 23 | 23 | 23 | 23 | 23 | 23 | OK | 28 | 28 | 28 | 28 | 28 | OK | 102 | 102 | 102 |  | 51
8 LEFT | 22 | 22 | 22 | 22 | 22 | 22 | OK | 19 | 19 | 19 | 19 | 19 | OK | 82 | 82 | 82 |  | 41
8 RIGHT | 23 | 23 | 23 | 23 | 23 | 23 | OK | 21 | 21 | 21 | 21 | 21 | OK | 88 | 88 | 88 |  | 44
Total | 360 | 360 | 360 | 360 | 360 | 360 |  | 309 | 309 | 309 | 309
in % |  | 100 | 100 | 100 | 100 | 100 |  |  | 100 | 100 | 100
Missing |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Sum BLECF complete installation |  |  |  |  | 669
Installed BLECF |  |  |  |  | 669 |  | in % | 100 | [11 empty] | updated 28.8.08
Missing BLECF complete installation |  |  |  |  | 0 |  | in % | 0
Note on F31: effinger: BYPLM.A17R5: Power supply 5V not working --> repaired, backplane was not soldered! --> Card is working and tested!
Note on F39: effinger: BJBHT.A32L7 220V missing --> Rack is connected to a closeby 220V power distribution

## Point 1
SR1 | Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | HV Levels | HV Levels | HV Levels | HV Levels | noise specta | [7 empty] | Modulation | [7 empty] | 10pA | [7 empty] | Expert Name
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Scan | Scan | Scan | Scan | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | other
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 21.09.09 |  | 13.10.09 |  |  |  | 13.10.09 | [12 empty] | 3.3.09 | 2.10.09 | 9.10.09 | 12.10.09 | Modulation 1: 8.10 and 12.10 |  | Comments
1 | BJBHT.A33L1 | BLECF_ | 285 | 0x | 011D | 6 | Arc | BYPLM.A33L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | I | 5 | 7-8 | BY02 | L | 1 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.15 (09-16)
2 | BJBHT.A32L1 | BLECF_ | 280 | 0x | 0118 | 6 | Arc | BYPLM.A32L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | I | 4 | 7-8 | BY02 | L | 1 | 19 | 15 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.15 (01-08)
3 | BJBHT.A31L1 | BLECF_ | 276 | 0x | 0114 | 6 | Arc | BYPLM.A31L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | I | 3 | 7-8 | BY02 | L | 1 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.14 (09-16)
4 | BJBHT.A30L1 | BLECF_ | 201 | 0x | 00C9 | 6 | Arc | BYPLM.A30L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | I | 2 | 7-8 | BY02 | L | 1 | 18 | 14 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.14 (01-08)
5 | BJBHT.A29L1 | BLECF_ | 141 | 0x | 008D | 6 | Arc | BYPLM.A29L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | I | 1 | 7-8 | BY02 | L | 1 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.13 (09-16)
6 | BJBHT.A28L1 | BLECF_ | 249 | 0x | 00F9 | 6 | Arc | BYPLM.A28L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | H | 6 | 7-8 | BY02 | L | 1 | 17 | 13 | 1-8 |  | ↑ | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.13 (01-08)
7 | BJBHT.A27L1 | BLECF_ | 241 | 0x | 00F1 | 6 | Arc | BYPLM.A27L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | H | 5 | 7-8 | BY02 | L | 1 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.12 (09-16)
8 | BJBHT.A26L1 | BLECF_ | 282 | 0x | 011A | 6 | Arc | BYPLM.A26L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 16 | 12 | 1-8 |  | ↑ | OK | ↑ | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.12 (01-08)
9 | BJBHT.A25L1 | BLECF_ | 218 | 0x | 00DA | 6 | Arc | BYPLM.A25L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | H | 3 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1408 | [27 empty] | CFV-SR1-BLML.BLETC.11 (09-16)
10 | BJBHT.A24L1 | BLECF_ | 204 | 0x | 00CC | 6 | Arc | BYPLM.A24L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | H | 2 | 7-8 | BY02 | L | 1 | 15 | 11 | 1-8 |  | OK | ↑ | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.11 (01-08)
11 | BJBHT.A23L1 | BLECF_ | 212 | 0x | 00D4 | 6 | Arc | BYPLM.A23L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.10 (09-16)
12 | BJBHT.A22L1 | BLECF_ | 284 | 0x | 011C | 6 | Arc | BYPLM.A22L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | G | 6 | 7-8 | BY02 | L | 1 | 14 | 10 | 1-8 |  | OK | ↑ | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.10 (01-08)
13 | BJBHT.A21L1 | BLECF_ | 22 | 0x | 0016 | 6 | Arc | BYPLM.A21L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1385 | 1266 | 1265 | [24 empty] | CFV-SR1-BLML.BLETC.09 (09-16) | bar: noise specta 1 to noise specta 6
14 | BJBHT.A20L1 | BLECF_ | 21 | 0x | 0015 | 6 | Arc | BYPLM.A20L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | G | 4 | 7-8 | BY02 | L | 1 | 13 | 9 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.09 (01-08) | bar: noise specta 1 to noise specta 6
15 | BJBHT.A19L1 | BLECF_ | 35 | 0x | 0023 | 6 | Arc | BYPLM.A19L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | G | 3 | 7-8 | BY02 | L | 1 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.08 (09-16) | bar: noise specta 1 to noise specta 6
16 | BJBHT.A18L1 | BLECF_ | 34 | 0x | 0022 | 6 | Arc | BYPLM.A18L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | G | 2 | 7-8 | BY02 | L | 1 | 11 | 8 | 1-8 |  | ↑ | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.08 (01-08) | bar: noise specta 1 to noise specta 8
17 | BJBHT.A17L1 | BLECF_ | 36 | 0x | 0024 | 6 | Arc | BYPLM.A17L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | G | 1 | 7-8 | BY02 | L | 1 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.07 (09-16) | bar: noise specta 1 to noise specta 6
18 | BJBHT.A16L1 | BLECF_ | 52 | 0x | 0034 | 6 | Arc | BYPLM.A16L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | F | 5 | 7-8 | BY02 | L | 1 | 10 | 7 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1394 | [27 empty] | CFV-SR1-BLML.BLETC.07 (01-08) | bar: noise specta 1 to noise specta 8
19 | BJBHT.A15L1 | BLECF_ | 59 | 0x | 003B | 6 | Arc | BYPLM.A15L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | F | 4 | 7-8 | BY02 | L | 1 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.06 (09-16) | bar: 10pA 1 to 10pA 3; 10pA 5 to 10pA 8
20 | BJBHT.A14L1 | BLECF_ | 58 | 0x | 003A | 6 | Arc | BYPLM.A14L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | F | 3 | 7-8 | BY02 | L | 1 | 9 | 6 | 1-8 |  | OK | ↑ | ↑ | OK |  |  | OK | OK | OK | OK | OK | [12 empty] | 10pA 4: to small value 300 BLMbits | CFV-SR1-BLML.BLETC.06 (01-08)
21 | BJBHT.A13L1 | BLECF_ | 77 | 0x | 004D | 8 | Arc | BYPLM.A13L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.05 (09-16)
22 | BJBHT.A12L1 | BLECF_ | 79 | 0x | 004F | 6 | Arc | BYPLM.A12L1 | 1 | L |  |  |  | 7-8 | SR1 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [10 empty] | 1383 | 1383 | [24 empty] | CFV-SR1-BLML.BLETC.05 (01-08)
23 | BJBHT.B11L1 | BLECF_ | 667 | 0x | 029B | 8 | RR13 | BY02 | 1 | CL | 2 | 9 | B | 13-14 | SR1 | BY05 | C | 4 | 1-2 | BY02 | L | 1 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.04 (09-16)
24 | BJBHT.A11L1 | BLECF_ | 594 | 0x | 0252 | 8 | RR13 | BY02 | 1 | CL | 2 | 8 | B | 11-12 | SR1 | BY05 | C | 3 | 11-12 | BY02 | C | 2 | 9 | 6 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.06 (01-08)
25 | BJBHT.B10L1 | BLECF_ | 409 | 0x | 0199 | 6 | RR13 | BY02 | 1 | CL | 2 | 7 | B | 9-10 | SR1 | BY05 | C | 3 | 9-10 | BY02 | L | 1 | 7 | 4 | 1-8 |  | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.04 (01-08)
26 | BJBHT.A10L1 | BLECF_ | 550 | 0x | 0226 | 2 | RR13 | BY02 | 1 | CL | 2 | 6 | B | 7-8 | SR1 | BY05 | C | 3 | 7-8 | BY02 | C | 2 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1394 | [27 empty] | CFV-SR1-BLMC.BLETC.05 (09-16)
27 | BJBHT.A9L1 | BLECF_ | 518 | 0x | 0206 | 6 | RR13 | BY02 | 1 | CL | 2 | 5 | B | 5-6 | SR1 | BY05 | C | 3 | 5-6 | BY02 | L | 1 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR1-BLML.BLETC.03 (09-16)
28 | BJBHT.B8L1 | BLECF_ | 457 | 0x | 01C9 | 6 | RR13 | BY02 | 1 | CL | 2 | 4 | B | 3-4 | SR1 | BY05 | C | 3 | 3-4 | BY02 | L | 1 | 6 | 3 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.03 (01-08)
29 | BJBHT.A8L1 | BLECF_ | 588 | 0x | 024C | 6 | RR13 | BY02 | 1 | CL | 2 | 3 | B | 1-2 | SR1 | BY05 | C | 3 | 1-2 | BY02 | C | 2 | 8 | 5 | 1-8 |  | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.05 (01-08)
30 | BJBHT.B7L1 | BLECF_ | 322 | 0x | 0142 | 7 | RR13 | BY02 | 1 | CL | 2 | 2 | A | 23-24 | SR1 | BY05 | C | 2 | 11-12 | BY02 | L | 1 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.02 (09-16)
31 | BJBHT.A7L1 | BLECF_ | 194 | 0x | 00C2 | 1 | RR13 | BY02 | 1 | CL | 2 | 1 | A | 21-22 | SR1 | BY05 | C | 2 | 9-10 | BY02 | C | 2 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.04 (09-16)
32 | BJBHT.A6L1 | BLECF_ | 638 | 0x | 027E | 6 | RR13 | BY02 | 1 | CL | 1 | 10 | A | 19-20 | SR1 | BY05 | C | 2 | 7-8 | BY02 | L | 1 | 5 | 2 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1299 | [26 empty] | CFV-SR1-BLML.BLETC.02 (01-08) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 3
33 | BJBHT.B5L1 | BLECF_ | 530 | 0x | 0212 | 7 | RR13 | BY02 | 1 | CL | 1 | 9 | A | 17-18 | SR1 | BY05 | C | 2 | 5-6 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.01 (09-16)
34 | BJBHT.A5L1 | BLECF_ | 597 | 0x | 0255 | 1 | RR13 | BY02 | 1 | CL | 1 | 8 | A | 15-16 | SR1 | BY05 | C | 2 | 3-4 | BY02 | C | 2 | 7 | 4 | 1-8 |  | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.04 (01-08) | bar: noise specta 1
35 | BJBHT.C4L1 | BLECF_ | 398 | 0x | 018E | 6 | RR13 | BY02 | 1 | CL | 1 | 7 | A | 13-14 | SR1 | BY05 | C | 2 | 1-2 | BY02 | L | 1 | 4 | 1 | 1-8 |  | OK | ↑ | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLML.BLETC.01 (01-08)
36 | BJBHT.B4L1 | BLECF_ | 374 | 0x | 0176 | 4 | RR13 | BY02 | 1 | CL | 1 | 6 | A | 11-12 | SR1 | BY05 | C | 1 | 11-12 | BY02 | C | 2 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.03 (09-16) | bar: noise specta 1 to noise specta 4
37 | BJBHT.A4L1 | BLECF_ | 595 | 0x | 0253 | 4 | RR13 | BY02 | 1 | CL | 1 | 5 | A | 9-10 | SR1 | BY05 | C | 1 | 9-10 | BY02 | C | 2 | 6 | 3 | 1-8 |  | OK | ↑ | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.03 (01-08)
38 | BJBHT.A3L1 | BLECF_ | 593 | 0x | 0251 | 5 | RR13 | BY02 | 1 | CL | 1 | 4 | A | 7-8 | SR1 | BY05 | C | 1 | 7-8 | BY02 | C | 2 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.02 (09-16)
39 | BJBHT.A2L1 | BLECF_ | 592 | 0x | 0250 | 8 | RR13 | BY02 | 1 | CL | 1 | 3 | A | 5-6 | SR1 | BY05 | C | 1 | 5-6 | BY02 | C | 2 | 5 | 2 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.02 (01-08)
40 | BJBHT.B1L1 | BLECF_ | 635 | 0x | 027B | 5 | RR13 | BY02 | 1 | CL | 1 | 2 | A | 3-4 | SR1 | BY05 | C | 1 | 3-4 | BY02 | C | 2 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.01 (09-16)
41 | BJBHT.A1L1 | BLECF_ | 639 | 0x | 027F | 1 | RR13 | BY02 | 1 | CL | 1 | 1 | A | 1-2 | SR1 | BY05 | C | 1 | 1-2 | BY02 | C | 2 | 4 | 1 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.01 (01-08)
42 | BJBHT.A1R1 | BLECF_ | 377 | 0x | 0179 | 1 | RR17 | BY02 | 1 | CR | 1 | 1 | A | 1-2 | SR1 | BY05 | C | 12 | 1-2 | BY02 | C | 2 | 13 | 9 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.09 (01-08) | bar: 10pA 2; 10pA 4
43 | BJBHT.B1R1 | BLECF_ | 331 | 0x | 014B | 5 | RR17 | BY02 | 1 | CR | 1 | 2 | A | 3-4 | SR1 | BY05 | C | 12 | 3-4 | BY02 | C | 2 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.09 (09-16)
44 | BJBHT.A2R1 | BLECF_ | 501 | 0x | 01F5 | 8 | RR17 | BY02 | 1 | CR | 1 | 3 | A | 5-6 | SR1 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.10 (01-08) | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: noise specta 2 to noise specta 8; Modulation 6 to Modulation 8; 10pA 4 to 10pA 5
45 | BJBHT.A3R1 | BLECF_ | 636 | 0x | 027C | 5 | RR17 | BY02 | 1 | CR | 1 | 4 | A | 7-8 | SR1 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.10 (09-16) | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: noise specta 2 to noise specta 5; Modulation 6 to Modulation 8; 10pA 5 to 10pA 6
46 | BJBHT.A4R1 | BLECF_ | 676 | 0x | 02A4 | 4 | RR17 | BY02 | 1 | CR | 1 | 5 | A | 9-10 | SR1 | BY05 | C | 12 | 9-10 | BY02 | C | 2 | 15 | 11 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.11 (01-08)
47 | BJBHT.B4R1 | BLECF_ | 653 | 0x | 028D | 4 | RR17 | BY02 | 1 | CR | 1 | 6 | A | 11-12 | SR1 | BY05 | C | 12 | 11-12 | BY02 | C | 2 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.11 (09-16) | bar: noise specta 1 to noise specta 4
48 | BJBHT.C4R1 | BLECF_ | 376 | 0x | 0178 | 6 | RR17 | BY02 | 1 | CR | 1 | 7 | A | 13-14 | SR1 | BY05 | C | 11 | 1-2 | BY02 | R | 3 | 4 | 1 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.01 (01-08)
49 | BJBHT.A5R1 | BLECF_ | 437 | 0x | 01B5 | 1 | RR17 | BY02 | 1 | CR | 1 | 8 | A | 15-16 | SR1 | BY05 | C | 11 | 3-4 | BY02 | C | 2 | 16 | 12 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.12 (01-08) | Jonathan and Ion: check in the tunnel necessary | bar: noise specta 1; Modulation 1
50 | BJBHT.B5R1 | BLECF_ | 442 | 0x | 01BA | 7 | RR17 | BY02 | 1 | CR | 1 | 9 | A | 17-18 | SR1 | BY05 | C | 11 | 5-6 | BY02 | R | 3 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.01 (09-16)
51 | BJBHT.A6R1 | BLECF_ | 383 | 0x | 017F | 6 | RR17 | BY02 | 1 | CR | 1 | 10 | A | 19-20 | SR1 | BY05 | C | 11 | 7-8 | BY02 | R | 3 | 5 | 2 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.02 (01-08)
52 | BJBHT.A7R1 | BLECF_ | 323 | 0x | 0143 | 1 | RR17 | BY02 | 1 | CR | 2 | 1 | A | 21-22 | SR1 | BY05 | C | 11 | 9-10 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.12 (09-16)
53 | BJBHT.B7R1 | BLECF_ | 512 | 0x | 0200 | 7 | RR17 | BY02 | 1 | CR | 2 | 2 | A | 23-24 | SR1 | BY05 | C | 11 | 11-12 | BY02 | R | 3 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.02 (09-16)
54 | BJBHT.A8R1 | BLECF_ | 325 | 0x | 0145 | 6 | RR17 | BY02 | 1 | CR | 2 | 3 | B | 1-2 | SR1 | BY05 | C | 10 | 1-2 | BY02 | C | 2 | 17 | 13 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.13 (01-08)
55 | BJBHT.B8R1 | BLECF_ | 647 | 0x | 0287 | 6 | RR17 | BY02 | 1 | CR | 2 | 4 | B | 3-4 | SR1 | BY05 | C | 10 | 3-4 | BY02 | R | 3 | 6 | 3 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.03 (01-08)
56 | BJBHT.A9R1 | BLECF_ | 85 | 0x | 0055 | 6 | RR17 | BY02 | 1 | CR | 2 | 5 | B | 5-6 | SR1 | BY05 | C | 10 | 5-6 | BY02 | R | 3 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1238 | [27 empty] | CFV-SR1-BLMR.BLETC.03 (09-16) | bar: noise specta 2 to noise specta 6
57 | BJBHT.A10R1 | BLECF_ | 338 | 0x | 0152 | 2 | RR17 | BY02 | 1 | CR | 2 | 6 | B | 7-8 | SR1 | BY05 | C | 10 | 7-8 | BY02 | C | 2 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.13 (09-16)
58 | BJBHT.B10R1 | BLECF_ | 567 | 0x | 0237 | 6 | RR17 | BY02 | 1 | CR | 2 | 7 | B | 9-10 | SR1 | BY05 | C | 10 | 9-10 | BY02 | R | 3 | 7 | 4 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.04 (01-08) | bar: noise specta 2 to noise specta 6
59 | BJBHT.A11R1 | BLECF_ | 349 | 0x | 015D | 8 | RR17 | BY02 | 1 | CR | 2 | 8 | B | 11-12 | SR1 | BY05 | C | 10 | 11-12 | BY02 | C | 2 | 18 | 14 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMC.BLETC.14 (01-08)
60 | BJBHT.B11R1 | BLECF_ | 327 | 0x | 0147 | 8 | RR17 | BY03 | 2 | CR | 2 | 9 | B | 13-14 | SR2 | BY06 | C | 9 | 1-2 | BY02 | R | 3 | 7 | 4 | 9-16 | Level blinking | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1303 | 1294 | [26 empty] | CFV-SR1-BLMR.BLETC.04 (09-16)
61 | BJBHT.A12R1 | BLECF_ | 539 | 0x | 021B | 6 | Arc | BYPLM.A12R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | F | 8 | 7-8 | BY02 | R | 3 | 8 | 5 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.05 (01-08)
62 | BJBHT.A13R1 | BLECF_ | 361 | 0x | 0169 | 8 | Arc | BYPLM.A13R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1301 | [27 empty] | CFV-SR1-BLMR.BLETC.05 (09-16)
63 | BJBHT.A14R1 | BLECF_ | 570 | 0x | 023A | 6 | Arc | BYPLM.A14R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | F | 10 | 7-8 | BY02 | R | 3 | 9 | 6 | 1-8 |  | OK | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.06 (01-08)
64 | BJBHT.A15R1 | BLECF_ | 306 | 0x | 0132 | 6 | Arc | BYPLM.A15R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | F | 11 | 7-8 | BY02 | R | 3 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1286 | [27 empty] | CFV-SR1-BLMR.BLETC.06 (09-16)
65 | BJBHT.A16R1 | BLECF_ | 311 | 0x | 0137 | 6 | Arc | BYPLM.A16R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | F | 12 | 7-8 | BY02 | R | 3 | 10 | 7 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.07 (01-08)
66 | BJBHT.A17R1 | BLECF_ | 303 | 0x | 012F | 6 | Arc | BYPLM.A17R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | G | 7 | 7-8 | BY02 | R | 3 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.07 (09-16)
67 | BJBHT.A18R1 | BLECF_ | 515 | 0x | 0203 | 6 | Arc | BYPLM.A18R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | G | 8 | 7-8 | BY02 | R | 3 | 11 | 8 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1294 | [27 empty] | CFV-SR1-BLMR.BLETC.08 (01-08)
68 | BJBHT.A19R1 | BLECF_ | 481 | 0x | 01E1 | 6 | Arc | BYPLM.A19R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | G | 9 | 7-8 | BY02 | R | 3 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.08 (09-16)
69 | BJBHT.A20R1 | BLECF_ | 317 | 0x | 013D | 6 | Arc | BYPLM.A20R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 |  | ↑ | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.09 (01-08)
70 | BJBHT.A21R1 | BLECF_ | 522 | 0x | 020A | 6 | Arc | BYPLM.A21R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.09 (09-16)
71 | BJBHT.A22R1 | BLECF_ | 373 | 0x | 0175 | 6 | Arc | BYPLM.A22R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | G | 12 | 7-8 | BY02 | R | 3 | 14 | 10 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.10 (01-08)
72 | BJBHT.A23R1 | BLECF_ | 423 | 0x | 01A7 | 6 | Arc | BYPLM.A23R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | H | 7 | 7-8 | BY02 | R | 3 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1406 | [27 empty] | CFV-SR1-BLMR.BLETC.10 (09-16)
73 | BJBHT.A24R1 | BLECF_ | 352 | 0x | 0160 | 6 | Arc | BYPLM.A24R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.11 (01-08)
74 | BJBHT.A25R1 | BLECF_ | 500 | 0x | 01F4 | 6 | Arc | BYPLM.A25R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | H | 9 | 7-8 | BY02 | R | 3 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1384 | 1297 | 1294 | [24 empty] | CFV-SR1-BLMR.BLETC.11 (09-16)
75 | BJBHT.A26R1 | BLECF_ | 479 | 0x | 01DF | 6 | Arc | BYPLM.A26R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | H | 10 | 7-8 | BY02 | R | 3 | 16 | 12 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.12 (01-08)
76 | BJBHT.A27R1 | BLECF_ | 478 | 0x | 01DE | 6 | Arc | BYPLM.A27R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1389 | [27 empty] | CFV-SR1-BLMR.BLETC.12 (09-16)
77 | BJBHT.A28R1 | BLECF_ | 304 | 0x | 0130 | 6 | Arc | BYPLM.A28R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | H | 12 | 7-8 | BY02 | R | 3 | 17 | 13 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.13 (01-08)
78 | BJBHT.A29R1 | BLECF_ | 310 | 0x | 0136 | 6 | Arc | BYPLM.A29R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.13 (09-16)
79 | BJBHT.A30R1 | BLECF_ | 329 | 0x | 0149 | 6 | Arc | BYPLM.A30R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | I | 8 | 7-8 | BY02 | R | 3 | 18 | 14 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.14 (01-08)
80 | BJBHT.A31R1 | BLECF_ | 495 | 0x | 01EF | 6 | Arc | BYPLM.A31R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | I | 9 | 7-8 | BY02 | R | 3 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1388 | [27 empty] | CFV-SR1-BLMR.BLETC.14 (09-16)
81 | BJBHT.A32R1 | BLECF_ | 384 | 0x | 0180 | 6 | Arc | BYPLM.A32R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | I | 10 | 7-8 | BY02 | R | 3 | 19 | 15 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.15 (01-08)
82 | BJBHT.A33R1 | BLECF_ | 417 | 0x | 01A1 | 6 | Arc | BYPLM.A33R1 | 1 | R |  |  |  | 7-8 | SR1 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR1-BLMR.BLETC.15 (09-16)
83 | BJBHT.A34R1 | BLECF_ | 321 | 0x | 0141 | 6 | Arc | BYPLM.A34R1 | 1 | R |  |  |  | 7-9 | SR1 | BY05 | I | 12 | 7-8 | BY02 | R | 3 | 20 | 16 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1392 | [27 empty] | CFV-SR1-BLMR.BLETC.16 (01-08)
last entry 18/6/08
[9 empty] | Transformer soldered | [40 empty] | noise specta 1: noise specta; Modulation 1: Modulation; 10pA 1: 10pA
[53 empty] | < 100 BLMbits | [7 empty] | o.k. | [7 empty] | o.k.
Card number correct
|  |  |  | 0x | 0000 | Card number needs to be checked | [43 empty] | noise specta 4: 100-300 BLMbits; Modulation 4: Prob. values mod; 10pA 4: to small values 20s
|  |  |  | 0x | 0000 | Card number unknown need to be checked in the tunnel
[53 empty] | > 300 BLMbits | [7 empty] | Prob. Data base | [7 empty] | Prob. to be checked
|  | BLECF_ | 656 | Card was exchanged, Data base need to be checked for the correct number
[53 empty] | > 522 BLMbits | [7 empty] | Flag missing in DB
[51 empty] | n |  | no data
Note on AV3: effinger: Repair 9beginning week 41 done by Ion scan necessary to vrrify
Note on AA12: effinger: 18.8.08 CFC was not working --> -5V broken (cable broken on the backplane) repaired --> no LF LF
Note on AJ12: effinger: ERRC at last check 21.09.09
Note on AL12: effinger: FID at last check 21.09.09
Note on T14: effinger: 13.08.08 need to check if the fibre are changed to 5-6 --> 18.8.08 was connected to 5&6 reconnected to 7&8
Note on AA14: effinger: 18.8.08 CFC was not working --> reset --> no LF LF
Note on AA15: effinger: Card replaced because channels 3 -6 blocked to negative: BLECF_0283 replaced by BLECF_0212
Note on AN18: effinger: Very rare level indication in ch4
Note on AP18: effinger: Ionisation chabmber replaced by Raymond and Ion (week 41 th), IC produced noise.
Note on AW26: effinger: Still o.k
Note on AA28: effinger: CFC test in the tunnel, all CFC were working, to cards A6L1 and B8L1 haven't been connected , all fibres were reconnected, CFC cards haven't been fixed with the screws -> done
Note on BI37: effinger: Lower phase value -> Johnatan need s to check
Note on AM40: effinger: Very high DAC values
Note on AM48: effinger: Level blinking -> NG18 cable repaired by R,R
Note on BP48: effinger: 40us->goes to 0
Note on BR48: effinger: 20s jumps to 4000 BLMbits
Note on AM50: effinger: Cable repaired bt I,R and R (week 41)
Note on BL50: jemery: Database or connetion problem
Note on BR50: effinger: 40us->goes to 0
Note on BS50: effinger: 40us->goes to 0
Note on BS51: effinger: 40us->goes to 0
Note on BT51: effinger: 40us->goes to 0
Note on AM52: effinger: Consantly level indication on in channel 5
Note on AQ52: effinger: Card repaired by Romain
Note on AJ54: effinger: ERRC at last check 21.09.09
Note on BG55: effinger: Lower phase value -> Johnatan need s to check
Note on AL62: effinger: FID at last check 21.09.09
Note on AJ64: effinger: ERRC at last check 21.09.09
Note on BN64: effinger: Glitch or crosstalk -> measurement repeated then o.k. !
Note on AL66: effinger: FID at last check 21.09.09
Note on AM66: effinger: Ch2 -Ch7 Level on and no signal in 40us but no CFC error!!!!!!! Checking of the card in the surface evt. Repairing of the card!
Note on AN66: effinger: NG18 signal cable replaced by Raymond, Ion and Romain
Note on AA68: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8
Note on AJ68: effinger: ERRC at last check 21.09.09
Note on AA69: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8
Note on AA70: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8
Note on AA71: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8
Note on AA72: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8 and CFC was not working after reset o.k.
Note on AA73: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8
Note on AA74: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8 and CFC was not working after reset o.k.
Note on AA75: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8
Note on AA76: effinger: fibre wrong connected in the tunnel 5&6 instead of 7&8
Note on AA77: effinger: 12.08.08 Fibre wrong connected 5&6 instead of 7&8, changed to 7&8 CFC o.k no LF
Note on T79: effinger: 13.08.08 need to check if the fibre are changed to 5-6 --> checked 18.8.08 connected to 7-8
Note on AA79: effinger: 12.08.08 CFC o.k no LF in the tunnel
Note on AA80: effinger:12.08.08 CFC not working -> reset -> CFC o.k no LF
Note on AA83: effinger: 12.08.08 Fibre wrong connected 5&6 instead of 7&8, changed to 7&8 CFC o.k no LF
Note on AA85: effinger: Card number rechecked in the tunnel : 310 installed
Note on AA86: effinger:12.08.08 Fibre wrong connected 5&6 instead of 7&8, one patch broken, changed to 7&8 CFC o.k no LF
Note on AA88: effinger: 12.08.08 Fibre wrong connected 5&6 instead of 7&8, changed to 7&8 CFC o.k no LF
Note on AA90: effinger: 12.08.08 Checked in the tunnel --> all o.k.
Note on D100: effinger: 565 original number chnaged to 656
Note on BH101: jemery: Spare for phase 2

## Point 2
SR2 | Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | HV Levels | HV Levels | HV Levels |  | noise specta | [7 empty] | Modulation | [7 empty] | 10pA | [7 empty] | Expert Name
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Scan 16.9.09 | Scan | Scan |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | other
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 22.09.09 |  | 13.10.09 |  |  |  | 13.10.09 | [13 empty] | 2.10.09 | 9.10.09 |  | noise specta 1: 10.10 and 12.10; Modulation 1: 8.10 and 12.10 |  | Comments
1 | BJBHT.A33L2 | BLECF_ | 399 | 0x | 018F | 6 | Arc | BYPLM.A33L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | I | 5 | 7-8 | BY02 | L | 1 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.15 (09-16)
2 | BJBHT.A32L2 | BLECF_ | 348 | 0x | 015C | 6 | Arc | BYPLM.A32L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | I | 4 | 7-8 | BY02 | L | 1 | 19 | 15 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [10 empty] | 1332 | 1330 | [24 empty] | CFV-SR2-BLML.BLETC.15 (01-08)
3 | BJBHT.A31L2 | BLECF_ | 497 | 0x | 01F1 | 6 | Arc | BYPLM.A31L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | I | 3 | 7-8 | BY02 | L | 1 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.14 (09-16)
4 | BJBHT.A30L2 | BLECF_ | 432 | 0x | 01B0 | 6 | Arc | BYPLM.A30L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | I | 2 | 7-8 | BY02 | L | 1 | 18 | 14 | 1-8 |  | OK | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.14 (01-08)
5 | BJBHT.A29L2 | BLECF_ | 520 | 0x | 0208 | 6 | Arc | BYPLM.A29L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | I | 1 | 7-8 | BY02 | L | 1 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.13 (09-16)
6 | BJBHT.A28L2 | BLECF_ | 439 | 0x | 01B7 | 6 | Arc | BYPLM.A28L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | H | 6 | 7-8 | BY02 | L | 1 | 17 | 13 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.13 (01-08) | bar: noise specta 2
7 | BJBHT.A27L2 | BLECF_ | 342 | 0x | 0156 | 6 | Arc | BYPLM.A27L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | H | 5 | 7-8 | BY02 | L | 1 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.12 (09-16)
8 | BJBHT.A26L2 | BLECF_ | 460 | 0x | 01CC | 6 | Arc | BYPLM.A26L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 16 | 12 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.12 (01-08) | bar: noise specta 6
9 | BJBHT.A25L2 | BLECF_ | 388 | 0x | 0184 | 6 | Arc | BYPLM.A25L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | H | 3 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.11 (09-16)
10 | BJBHT.A24L2 | BLECF_ | 440 | 0x | 01B8 | 6 | Arc | BYPLM.A24L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | H | 2 | 7-8 | BY02 | L | 1 | 15 | 11 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.11 (01-08)
11 | BJBHT.A23L2 | BLECF_ | 468 | 0x | 01D4 | 6 | Arc | BYPLM.A23L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.10 (09-16)
12 | BJBHT.A22L2 | BLECF_ | 456 | 0x | 01C8 | 6 | Arc | BYPLM.A22L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | G | 6 | 7-8 | BY02 | L | 1 | 14 | 10 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.10 (01-08)
13 | BJBHT.A21L2 | BLECF_ | 111 | 0x | 006F | 6 | Arc | BYPLM.A21L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.09 (09-16)
14 | BJBHT.A20L2 | BLECF_ | 11 | 0x | 000B | 6 | Arc | BYPLM.A20L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | G | 4 | 7-8 | BY02 | L | 1 | 13 | 9 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.09 (01-08)
15 | BJBHT.A19L2 | BLECF_ | 715 | 0x | 02CB | 6 | Arc | BYPLM.A19L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | G | 3 | 7-8 | BY02 | L | 1 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.08 (09-16)
16 | BJBHT.A18L2 | BLECF_ | 366 | 0x | 016E | 6 | Arc | BYPLM.A18L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | G | 2 | 7-8 | BY02 | L | 1 | 11 | 8 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.08 (01-08)
17 | BJBHT.A17L2 | BLECF_ | 427 | 0x | 01AB | 6 | Arc | BYPLM.A17L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | G | 1 | 7-8 | BY02 | L | 1 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.07 (09-16)
18 | BJBHT.A16L2 | BLECF_ | 385 | 0x | 0181 | 6 | Arc | BYPLM.A16L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | F | 5 | 7-8 | BY02 | L | 1 | 10 | 7 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.07 (01-08)
19 | BJBHT.A15L2 | BLECF_ | 444 | 0x | 01BC | 6 | Arc | BYPLM.A15L2 | 2 | L |  |  |  | 5-6 | SR2 | BY05 | F | 4 | 5-6 | BY02 | L | 1 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.06 (09-16)
20 | BJBHT.A14L2 | BLECF_ | 380 | 0x | 017C | 6 | Arc | BYPLM.A14L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | F | 3 | 7-8 | BY02 | L | 1 | 9 | 6 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.06 (01-08)
21 | BJBHT.A13L2 | BLECF_ | 347 | 0x | 015B | 6 | Arc | BYPLM.A13L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.05 (09-16)
22 | BJBHT.A12L2 | BLECF_ | 200 | 0x | 00C8 | 8 | Arc | BYPLM.A12L2 | 2 | L |  |  |  | 7-8 | SR2 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.05 (01-08)
23 | BJBHT.C11L2 | BLECF_ | 583 | 0x | 0247 | 6 | UA23 | BY02 | 2 | CL | 3 | 2 | C | 19-20 | SR2 | BY05 | C | 4 | 7-8 | BY02 | L | 1 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.04 (09-16)
24 | BJBHT.B11L2 | BLECF_ | 343 | 0x | 0157 | 6 | UA23 | BY02 | 2 | CL | 3 | 1 | C | 17-18 | SR2 | BY05 | C | 4 | 5-6 | BY02 | C | 2 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.07 (09-16) | Slava: Expert name missing in MTF | bar: noise specta 1 to noise specta 6; Modulation 7
25 | BJBHT.A11L2 | BLECF_ | 378 | 0x | 017A | 6 | UA23 | BY02 | 2 | CL | 2 | 10 | C | 15-16 | SR2 | BY05 | C | 4 | 3-4 | BY02 | C | 2 | 10 | 7 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [10 empty] | up o.k. down not o.k | up o.k. down not o.k | [24 empty] | CFV-SR2-BLMC.BLETC.07 (01-08)
26 | BJBHT.B10L2 | BLECF_ | 134 | 0x | 0086 | 6 | UA23 | BY02 | 2 | CL | 2 | 9 | C | 13-14 | SR2 | BY05 | C | 4 | 1-2 | BY02 | L | 1 | 7 | 4 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.04 (01-08) | bar: noise specta 1 to noise specta 6
27 | BJBHT.A10L2 | BLECF_ | 50 | 0x | 0032 | 7 | UA23 | BY02 | 2 | CL | 2 | 8 | C | 11-12 | SR2 | BY05 | C | 3 | 11-12 | BY02 | C | 2 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.06 (09-16) | bar: noise specta 1 to noise specta 7
28 | BJBHT.A9L2 | BLECF_ | 517 | 0x | 0205 | 6 | UA23 | BY02 | 2 | CL | 2 | 7 | C | 9-10 | SR2 | BY05 | C | 3 | 9-10 | BY02 | L | 1 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.03 (09-16)
29 | BJBHT.C8L2 | BLECF_ | 357 | 0x | 0165 | 6 | UA23 | BY02 | 2 | CL | 2 | 6 | C | 7-8 | SR2 | BY05 | C | 3 | 7-8 | BY02 | L | 1 | 6 | 3 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.03 (01-08)
30 | BJBHT.B8L2 | BLECF_ | 333 | 0x | 014D | 6 | UA23 | BY02 | 2 | CL | 2 | 5 | C | 5-6 | SR2 | BY05 | C | 3 | 5-6 | BY02 | C | 2 | 9 | 6 | 1-8 |  | OK | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1319 |  | 1313 | [24 empty] | CFV-SR2-BLMC.BLETC.06 (01-08) | bar: noise specta 1 to noise specta 6
31 | BJBHT.A8L2 | BLECF_ | 491 | 0x | 01EB | 6 | UA23 | BY02 | 2 | CL | 2 | 4 | C | 3-4 | SR2 | BY05 | C | 3 | 3-4 | BY02 | C | 2 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.05 (09-16)
32 | BJBHT.A7L2 | BLECF_ | 362 | 0x | 016A | 6 | UA23 | BY02 | 2 | CL | 2 | 3 | C | 1-2 | SR2 | BY05 | C | 3 | 1-2 | BY02 | L | 1 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.02 (09-16)
33 | BJBHT.C6L2 | BLECF_ | 189 | 0x | 00BD | 6 | UA23 | BY02 | 2 | CL | 2 | 2 | B | 23-24 | SR2 | BY05 | C | 2 | 11-12 | BY02 | L | 1 | 5 | 2 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.02 (01-08)
34 | BJBHT.B6L2 | BLECF_ | 344 | 0x | 0158 | 6 | UA23 | BY02 | 2 | CL | 2 | 1 | B | 21-22 | SR2 | BY05 | C | 2 | 9-10 | BY02 | C | 2 | 8 | 5 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.05 (01-08) | bar: noise specta 1 to noise specta 6
35 | BJBHT.A6L2 | BLECF_ | 474 | 0x | 01DA | 6 | UA23 | BY02 | 2 | CL | 1 | 10 | B | 19-20 | SR2 | BY05 | C | 2 | 7-8 | BY02 | C | 2 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.04 (09-16)
36 | BJBHT.A5L2 | BLECF_ | 328 | 0x | 0148 | 6 | UA23 | BY02 | 2 | CL | 1 | 9 | B | 17-18 | SR2 | BY05 | C | 2 | 5-6 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR2-BLML.BLETC.01 (09-16)
37 | BJBHT.D4L2 | BLECF_ | 371 | 0x | 0173 | 8 | UA23 | BY02 | 2 | CL | 1 | 8 | B | 15-16 | SR2 | BY05 | C | 2 | 3-4 | BY02 | L | 1 | 4 | 1 | 1-8 |  | OK | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLML.BLETC.01 (01-08)
38 | BJBHT.C4L2 | BLECF_ | 181 | 0x | 00B5 | 1 | UA23 | BY02 | 2 | CL | 1 | 7 | B | 13-14 | SR2 | BY05 | C | 2 | 1-2 | BY02 | C | 2 | 7 | 4 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.04 (01-08) | bar: noise specta 1
39 | BJBHT.B4L2 | BLECF_ | 320 | 0x | 0140 | 4 | UA23 | BY02 | 2 | CL | 1 | 6 | B | 11-12 | SR2 | BY05 | C | 1 | 11-12 | BY02 | C | 2 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.03 (09-16) | bar: noise specta 1 to noise specta 4
40 | BJBHT.A4L2 | BLECF_ | 516 | 0x | 0204 | 7 | UA23 | BY02 | 2 | CL | 1 | 5 | B | 9-10 | SR2 | BY05 | C | 1 | 9-10 | BY02 | C | 2 | 6 | 3 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.03 (01-08)
41 | BJBHT.A3L2 | BLECF_ | 324 | 0x | 0144 | 4 | UA23 | BY02 | 2 | CL | 1 | 4 | B | 7-8 | SR2 | BY05 | C | 1 | 7-8 | BY02 | C | 2 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.02 (09-16)
42 | BJBHT.A2L2 | BLECF_ | 188 | 0x | 00BC | 8 | UA23 | BY02 | 2 | CL | 1 | 3 | B | 5-6 | SR2 | BY05 | C | 1 | 5-6 | BY02 | C | 2 | 5 | 2 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.02 (01-08)
43 | BJBHT.B1L2 | BLECF_ | 510 | 0x | 01FE | 5 | UA23 | BY02 | 2 | CL | 1 | 2 | B | 3-4 | SR2 | BY05 | C | 1 | 3-4 | BY02 | C | 2 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.01 (09-16)
44 | BJBHT.A1L2 | BLECF_ | 476 | 0x | 01DC | 1 | UA23 | BY02 | 2 | CL | 1 | 1 | B | 1-2 | SR2 | BY05 | C | 1 | 1-2 | BY02 | C | 2 | 4 | 1 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.01 (01-08)
45 | BJBHT.A1R2 | BLECF_ | 706 | 0x | 02C2 | 1 | UA27 | BY03 | 2 | CR | 1 | 1 | B | 1-2 | SR2 | BY05 | C | 12 | 1-2 | BY02 | C | 2 | 13 | 9 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.09 (01-08) | bar: noise specta 1
46 | BJBHT.B1R2 | BLECF_ | 606 | 0x | 025E | 5 | UA27 | BY03 | 2 | CR | 1 | 2 | B | 3-4 | SR2 | BY05 | C | 12 | 3-4 | BY02 | C | 2 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.09 (09-16) | bar: noise specta 2 to noise specta 5
47 | BJBHT.A2R2 | BLECF_ | 675 | 0x | 02A3 | 8 | UA27 | BY03 | 2 | CR | 1 | 3 | B | 5-6 | SR2 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.10 (01-08) | bar: noise specta 1 to noise specta 8
48 | BJBHT.A3R2 | BLECF_ | 641 | 0x | 0281 | 4 | UA27 | BY03 | 2 | CR | 1 | 4 | B | 7-8 | SR2 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.10 (09-16)
49 | BJBHT.A4R2 | BLECF_ | 719 | 0x | 02CF | 5 | UA27 | BY03 | 2 | CR | 1 | 5 | B | 9-10 | SR2 | BY05 | C | 12 | 9-10 | BY02 | C | 2 | 15 | 11 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [10 empty] | 1332 | 1333 | [24 empty] | CFV-SR2-BLMC.BLETC.11 (01-08)
50 | BJBHT.B4R2 | BLECF_ | 738 | 0x | 02E2 | 2 | UA27 | BY03 | 2 | CR | 1 | 6 | B | 11-12 | SR2 | BY05 | C | 12 | 11-12 | BY02 | C | 2 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.11 (09-16) | bar: noise specta 1 to noise specta 2
51 | BJBHT.C4R2 | BLECF_ | 652 | 0x | 028C | 1 | UA27 | BY03 | 2 | CR | 1 | 7 | B | 13-14 | SR2 | BY05 | C | 11 | 1-2 | BY02 | C | 2 | 16 | 12 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.12 (01-08) | bar: noise specta 1
52 | BJBHT.D4R2 | BLECF_ | 665 | 0x | 0299 | 8 | UA27 | BY03 | 2 | CR | 1 | 8 | B | 15-16 | SR2 | BY05 | C | 11 | 3-4 | BY02 | R | 3 | 4 | 1 | 1-8 |  | OK | ↑ | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.01 (01-08)
53 | BJBHT.A5R2 | BLECF_ | 740 | 0x | 02E4 | 6 | UA27 | BY03 | 2 | CR | 1 | 9 | B | 17-18 | SR2 | BY05 | C | 11 | 5-6 | BY02 | R | 3 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.01 (09-16)
54 | BJBHT.A6R2 | BLECF_ | 666 | 0x | 029A | 1 | UA27 | BY03 | 2 | CR | 1 | 10 | B | 19-20 | SR2 | BY05 | C | 11 | 7-8 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.12 (09-16) | bar: noise specta 1
55 | BJBHT.B6R2 | BLECF_ | 722 | 0x | 02D2 | 7 | UA27 | BY03 | 2 | CR | 2 | 1 | B | 21-22 | SR2 | BY05 | C | 11 | 9-10 | BY02 | R | 3 | 5 | 2 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.02 (01-08)
56 | BJBHT.A7R2 | BLECF_ | 658 | 0x | 0292 | 6 | UA27 | BY03 | 2 | CR | 2 | 2 | B | 23-24 | SR2 | BY05 | C | 11 | 11-12 | BY02 | R | 3 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.02 (09-16)
57 | BJBHT.A8R2 | BLECF_ | 626 | 0x | 0272 | 6 | UA27 | BY03 | 2 | CR | 2 | 3 | C | 1-2 | SR2 | BY05 | C | 10 | 1-2 | BY02 | C | 2 | 17 | 13 | 1-8 | Check of TC | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.13 (01-08)
58 | BJBHT.B8R2 | BLECF_ | 406 | 0x | 0196 | 6 | UA27 | BY03 | 2 | CR | 2 | 4 | C | 3-4 | SR2 | BY05 | C | 10 | 3-4 | BY02 | C | 2 | 17 | 13 | 9-16 | Check of TC | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.13 (09-16) | bar: noise specta 1 to noise specta 6
59 | BJBHT.C8R2 | BLECF_ | 4 | 0x | 0004 | 6 | UA27 | BY03 | 2 | CR | 2 | 5 | C | 5-6 | SR2 | BY05 | C | 10 | 5-6 | BY02 | R | 3 | 6 | 3 | 1-8 | Check of TC | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.03 (01-08)
60 | BJBHT.A9R2 | BLECF_ | 279 | 0x | 0117 | 6 | UA27 | BY03 | 2 | CR | 2 | 6 | C | 7-8 | SR2 | BY05 | C | 10 | 7-8 | BY02 | R | 3 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.03 (09-16) | Romain & Ewald: removing of the splitter (spare fibre)
61 | BJBHT.A10R2 | BLECF_ | 97 | 0x | 0061 | 6 | UA27 | BY03 | 2 | CR | 2 | 7 | C | 9-10 | SR2 | BY05 | C | 10 | 9-10 | BY02 | C | 2 | 18 | 14 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.14 (01-08) | bar: noise specta 1 to noise specta 6
62 | BJBHT.B10R2 | BLECF_ | 721 | 0x | 02D1 | 6 | UA27 | BY03 | 2 | CR | 2 | 8 | C | 11-12 | SR2 | BY05 | C | 10 | 11-12 | BY02 | R | 3 | 7 | 4 | 1-8 |  | OK | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.04 (01-08)
63 | BJBHT.A11R2 | BLECF_ | 128 | 0x | 0080 | 6 | UA27 | BY03 | 2 | CR | 2 | 9 | C | 13-14 | SR2 | BY05 | C | 9 | 1-2 | BY02 | C | 2 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.14 (09-16) | bar: noise specta 1 to noise specta 6
64 | BJBHT.B11R2 | BLECF_ | 627 | 0x | 0273 | 6 | UA27 | BY03 | 2 | CR | 2 | 10 | C | 15-16 | SR2 | BY05 | C | 9 | 3-4 | BY02 | C | 2 | 19 | 15 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMC.BLETC.15 (01-08) | Slava: Expert name missing in MTF | bar: noise specta 1 to noise specta 6; Modulation 7
65 | BJBHT.C11R2 | BLECF_ | 689 | 0x | 02B1 | 6 | UA27 | BY03 | 2 | CR | 3 | 1 | C | 17-18 | SR2 | BY05 | C | 9 | 5-6 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.04 (09-16)
66 | BJBHT.A12R2 | BLECF_ | 681 | 0x | 02A9 | 8 | Arc | BYPLM.A12R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | F | 8 | 7-8 | BY02 | R | 3 | 8 | 5 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.05 (01-08)
67 | BJBHT.A13R2 | BLECF_ | 687 | 0x | 02AF | 6 | Arc | BYPLM.A13R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.05 (09-16)
68 | BJBHT.A14R2 | BLECF_ | 684 | 0x | 02AC | 6 | Arc | BYPLM.A14R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | F | 10 | 7-8 | BY02 | R | 3 | 9 | 6 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.06 (01-08)
69 | BJBHT.A15R2 | BLECF_ | 484 | 0x | 01E4 | 6 | Arc | BYPLM.A15R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | F | 11 | 7-8 | BY02 | R | 3 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.06 (09-16)
70 | BJBHT.A16R2 | BLECF_ | 686 | 0x | 02AE | 6 | Arc | BYPLM.A16R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | F | 12 | 7-8 | BY02 | R | 3 | 10 | 7 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.07 (01-08)
71 | BJBHT.A17R2 | BLECF_ | 143 | 0x | 008F | 6 | Arc | BYPLM.A17R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | G | 7 | 7-8 | BY02 | R | 3 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.07 (09-16)
72 | BJBHT.A18R2 | BLECF_ | 463 | 0x | 01CF | 6 | Arc | BYPLM.A18R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | G | 8 | 7-8 | BY02 | R | 3 | 11 | 8 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.08 (01-08)
73 | BJBHT.A19R2 | BLECF_ | 379 | 0x | 017B | 6 | Arc | BYPLM.A19R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | G | 9 | 7-8 | BY02 | R | 3 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.08 (09-16)
74 | BJBHT.A20R2 | BLECF_ | 382 | 0x | 017E | 6 | Arc | BYPLM.A20R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 |  | OK | ↑ | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.09 (01-08)
75 | BJBHT.A21R2 | BLECF_ | 451 | 0x | 01C3 | 6 | Arc | BYPLM.A21R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.09 (09-16)
76 | BJBHT.A22R2 | BLECF_ | 404 | 0x | 0194 | 6 | Arc | BYPLM.A22R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | G | 12 | 7-8 | BY02 | R | 3 | 14 | 10 | 1-8 |  | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.10 (01-08)
77 | BJBHT.A23R2 | BLECF_ | 84 | 0x | 0054 | 6 | Arc | BYPLM.A23R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | H | 7 | 7-8 | BY02 | R | 3 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.10 (09-16) | bar: noise specta 4
78 | BJBHT.A24R2 | BLECF_ | 418 | 0x | 01A2 | 6 | Arc | BYPLM.A24R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.11 (01-08)
79 | BJBHT.A25R2 | BLECF_ | 390 | 0x | 0186 | 6 | Arc | BYPLM.A25R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | H | 9 | 7-8 | BY02 | R | 3 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.11 (09-16)
80 | BJBHT.A26R2 | BLECF_ | 214 | 0x | 00D6 | 6 | Arc | BYPLM.A26R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | H | 10 | 7-8 | BY02 | R | 3 | 16 | 12 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.12 (01-08)
81 | BJBHT.A27R2 | BLECF_ | 694 | 0x | 02B6 | 6 | Arc | BYPLM.A27R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.12 (09-16)
82 | BJBHT.A28R2 | BLECF_ | 685 | 0x | 02AD | 6 | Arc | BYPLM.A28R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | H | 12 | 7-8 | BY02 | R | 3 | 17 | 13 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.13 (01-08)
83 | BJBHT.A29R2 | BLECF_ | 725 | 0x | 02D5 | 6 | Arc | BYPLM.A29R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.13 (09-16)
84 | BJBHT.A30R2 | BLECF_ | 195 | 0x | 00C3 | 6 | Arc | BYPLM.A30R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | I | 8 | 7-8 | BY02 | R | 3 | 18 | 14 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.14 (01-08)
85 | BJBHT.A31R2 | BLECF_ | 690 | 0x | 02B2 | 6 | Arc | BYPLM.A31R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | I | 9 | 7-8 | BY02 | R | 3 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.14 (09-16)
86 | BJBHT.A32R2 | BLECF_ | 360 | 0x | 0168 | 6 | Arc | BYPLM.A32R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | I | 10 | 7-8 | BY02 | R | 3 | 19 | 15 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.15 (01-08)
87 | BJBHT.A33R2 | BLECF_ | 23 | 0x | 0017 | 6 | Arc | BYPLM.A33R2 | 2 | R |  |  |  | 7-8 | SR2 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.15 (09-16) | bar: noise specta 1 to noise specta 2; noise specta 5 to noise specta 6
88 | BJBHT.A34R2 | BLECF_ | 724 | 0x | 02D4 | 6 | Arc | BYPLM.A34R2 | 2 | R |  |  |  | 7-9 | SR2 | BY05 | I | 12 | 7-8 | BY02 | R | 3 | 20 | 16 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR2-BLMR.BLETC.16 (01-08)
last entry 17/6/08
Transformer soldered
[50 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA
[6 empty] | Card number correct | [43 empty] | noise specta 4: < 100 BLMbits; Modulation 4: o.k.; 10pA 4: o.k.
|  |  |  | 0x | 0000 | Card number needs to be checked
|  |  |  | 0x | 0000 | Card number unknown need to be checked in the tunnel | [43 empty] | noise specta 4: 100-300 BLMbits; Modulation 4: Prob. values mod; 10pA 4: to small values 20s
|  | BLECF_ | 656 | Card was exchanged, Data base need to be checked for the correct number | [45 empty] | noise specta 4: > 300 BLMbits; Modulation 4: Prob. Data base; 10pA 4: Prob. to be checked
[53 empty] | > 522 BLMbits | [7 empty] | Flag missing in DB
[51 empty] | n |  | no data
Note on AW6: effinger: O.K.
Note on AA7: effinger: CFC-Card not working: ->reset -> o.k. no LF on both
Note on AA9: effinger: CFC-Card not working: ->reset -> o.k. no LF on both
Note on T23: effinger: Fibre 7 & 8 broken, spare fibre used
Note on AA23: effinger: fibre connected to 5&6 -> reconnected to 7&8; CFC-Card working --> fibre 7 & 8 broken -> reconnected to 5 & 6
Note on AH29: effinger: LF on both cahnnels, after reset with HV o.k.!! 22.9.09
Note on BM29: jemery: MTF entry missing: Babara momitors
Note on AJ30: effinger: ERRC while check 22.09.09
Note on AX30: effinger: Needs to be checked with expertapplication
Note on BF32: effinger: A lot of noise on all channels
Note on AV35: effinger: on the limit but still o.k
Note on AU41: effinger: was o.k on the scan 3.09.09
Note on AJ43: effinger: ERRC while check 22.09.09
Note on AP52: effinger: CH 4,5,6 run sum 11 between 4000 and 6000 BLMbits
Note on AW55: effinger: O.K.
Note on AA63: effinger:
Note on AA65: effinger: CFC-Card working: -> o.k. no LF on both
Note on Z66: effinger: Splitter used!
Note on AJ67: effinger: ERRC while check 22.09.09
Note on BM70: jemery: MTF entry missing: Babara momitors
Note on AA75: effinger: CFC - Card working; no LF ; one Patch cord broken --> no LF on the both
Note on AA81: effinger: Card number checked: --> BLECF_0382 installed; sent number 382
Note on D105: effinger: 565 original number chnaged to 656
Note on BH107: jemery: Spare for phase 2

## Point 3
SR3 | Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | HV Levels | HV Levels | HV Levels | HV Levels | noise specta | [7 empty] | Modulation | [7 empty] | 10pA | [7 empty] | Expert Name
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Scan | Scan | Scan | Scan | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | other
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 22.09.09 |  | 13.10.09 |  |  |  | 22.09.09 | [12 empty] | 3.9.09 | 16.09.09 | 22.09.09 | 2.10.09 | noise specta 1: 10.10 and 12.10; Modulation 1: 8.10 and 12.10 |  | Comments
1 | BJBHT.A33L3 | BLECF_ | 619 | 0x | 026B | 6 | Arc | BYPLM.A33L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | I | 5 | 7-8 | BY02 | L | 1 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.15 (09-16)
2 | BJBHT.A32L3 | BLECF_ | 601 | 0x | 0259 | 6 | Arc | BYPLM.A32L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | I | 4 | 7-8 | BY02 | L | 1 | 19 | 15 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.15 (01-08)
3 | BJBHT.A31L3 | BLECF_ | 727 | 0x | 02D7 | 6 | Arc | BYPLM.A31L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | I | 3 | 7-8 | BY02 | L | 1 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.14 (09-16)
4 | BJBHT.A30L3 | BLECF_ | 705 | 0x | 02C1 | 6 | Arc | BYPLM.A30L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | I | 2 | 7-8 | BY02 | L | 1 | 18 | 14 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.14 (01-08)
5 | BJBHT.A29L3 | BLECF_ | 646 | 0x | 0286 | 6 | Arc | BYPLM.A29L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | I | 1 | 7-8 | BY02 | L | 1 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.13 (09-16)
6 | BJBHT.A28L3 | BLECF_ | 702 | 0x | 02BE | 6 | Arc | BYPLM.A28L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | H | 6 | 7-8 | BY02 | L | 1 | 17 | 13 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.13 (01-08)
7 | BJBHT.A27L3 | BLECF_ | 607 | 0x | 025F | 6 | Arc | BYPLM.A27L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | H | 5 | 7-8 | BY02 | L | 1 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.12 (09-16)
8 | BJBHT.A26L3 | BLECF_ | 623 | 0x | 026F | 6 | Arc | BYPLM.A26L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 16 | 12 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.12 (01-08)
9 | BJBHT.A25L3 | BLECF_ | 717 | 0x | 02CD | 6 | Arc | BYPLM.A25L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | H | 3 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.11 (09-16)
10 | BJBHT.A24L3 | BLECF_ | 319 | 0x | 013F | 6 | Arc | BYPLM.A24L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | H | 2 | 7-8 | BY02 | L | 1 | 15 | 11 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.11 (01-08)
11 | BJBHT.A23L3 | BLECF_ | 730 | 0x | 02DA | 6 | Arc | BYPLM.A23L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.10 (09-16)
12 | BJBHT.A22L3 | BLECF_ | 645 | 0x | 0285 | 6 | Arc | BYPLM.A22L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | G | 6 | 7-8 | BY02 | L | 1 | 14 | 10 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.10 (01-08)
13 | BJBHT.A21L3 | BLECF_ | 741 | 0x | 02E5 | 6 | Arc | BYPLM.A21L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.09 (09-16)
14 | BJBHT.A20L3 | BLECF_ | 614 | 0x | 0266 | 6 | Arc | BYPLM.A20L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | G | 4 | 7-8 | BY02 | L | 1 | 13 | 9 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.09 (01-08)
15 | BJBHT.A19L3 | BLECF_ | 620 | 0x | 026C | 6 | Arc | BYPLM.A19L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | G | 3 | 7-8 | BY02 | L | 1 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.08 (09-16)
16 | BJBHT.A18L3 | BLECF_ | 720 | 0x | 02D0 | 6 | Arc | BYPLM.A18L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | G | 2 | 7-8 | BY02 | L | 1 | 11 | 8 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.08 (01-08)
17 | BJBHT.A17L3 | BLECF_ | 668 | 0x | 029C | 6 | Arc | BYPLM.A17L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | G | 1 | 7-8 | BY02 | L | 1 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.07 (09-16)
18 | BJBHT.A16L3 | BLECF_ | 604 | 0x | 025C | 6 | Arc | BYPLM.A16L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | F | 5 | 7-8 | BY02 | L | 1 | 10 | 7 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.07 (01-08)
19 | BJBHT.A15L3 | BLECF_ | 622 | 0x | 026E | 6 | Arc | BYPLM.A15L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | F | 4 | 7-8 | BY02 | L | 1 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.06 (09-16)
20 | BJBHT.A14L3 | BLECF_ | 305 | 0x | 0131 | 6 | Arc | BYPLM.A14L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | F | 3 | 7-8 | BY02 | L | 1 | 9 | 6 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.06 (01-08)
21 | BJBHT.A13L3 | BLECF_ | 600 | 0x | 0258 | 10 | Arc | BYPLM.A13L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.05 (09-16)
22 | BJBHT.A12L3 | BLECF_ | 703 | 0x | 02BF | 10 | Arc | BYPLM.A12L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.05 (01-08)
23 | BJBHT.B11L3 | BLECF_ | 657 | 0x | 0291 | 7 | UJ33 | BY02 | 3 | L | 2 | 8 | C | 11-12 | SR3 | BY05 | C | 3 | 11-12 | BY02 | L | 1 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.04 (09-16) | High voltage modulation shows monitors disconnected
24 | BJBHT.A11L3 | BLECF_ | 654 | 0x | 028E | 12 | UJ33 | BY02 | 3 | L | 2 | 7 | C | 9-10 | SR3 | BY05 | C | 3 | 9-10 | BY02 | C | 2 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.05 (09-16) | High voltage modulation shows monitors disconnected
25 | BJBHT.A10L3 | BLECF_ | 674 | 0x | 02A2 | 11 | UJ33 | BY02 | 3 | L | 2 | 6 | C | 7-8 | SR3 | BY05 | C | 3 | 7-8 | BY02 | L | 1 | 7 | 4 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.04 (01-08) | High voltage modulation shows monitors disconnected | bar: noise specta 1 to noise specta 8
26 | BJBHT.B9L3 | BLECF_ | 754 | 0x | 02F2 | 11 | UJ33 | BY02 | 3 | L | 2 | 5 | C | 5-6 | SR3 | BY05 | C | 3 | 5-6 | BY02 | L | 1 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.03 (09-16)
27 | BJBHT.A9L3 | BLECF_ | 609 | 0x | 0261 | 10 | UJ33 | BY02 | 3 | L | 2 | 4 | C | 3-4 | SR3 | BY05 | C | 3 | 3-4 | BY02 | C | 2 | 8 | 5 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1323 | [27 empty] | CFV-SR3-BLMC.BLETC.05 (01-08)
28 | BJBHT.B8L3 | BLECF_ | 672 | 0x | 02A0 | 6 | UJ33 | BY02 | 3 | L | 2 | 3 | C | 1-2 | SR3 | BY05 | C | 3 | 1-2 | BY02 | L | 1 | 6 | 3 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.03 (01-08) | High voltage modulation shows monitors disconnected
29 | BJBHT.A8L3 | BLECF_ | 574 | 0x | 023E | 6 | UJ33 | BY02 | 3 | L | 2 | 2 | B | 23-24 | SR3 | BY05 | C | 2 | 11-12 | BY02 | C | 2 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.04 (09-16)
30 | BJBHT.B7L3 | BLECF_ | 576 | 0x | 0240 | 7 | UJ33 | BY02 | 3 | L | 2 | 1 | B | 21-22 | SR3 | BY05 | C | 2 | 9-10 | BY02 | L | 1 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.02 (09-16)
31 | BJBHT.A7L3 | BLECF_ | 637 | 0x | 027D | 1 | UJ33 | BY02 | 3 | L | 1 | 10 | B | 19-20 | SR3 | BY05 | C | 2 | 7-8 | BY02 | C | 2 | 7 | 4 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.04 (01-08) | bar: noise specta 1
32 | BJBHT.C6L3 | BLECF_ | 211 | 0x | 00D3 | 6 | UJ33 | BY02 | 3 | L | 1 | 9 | B | 17-18 | SR3 | BY05 | C | 2 | 5-6 | BY02 | L | 1 | 5 | 2 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.02 (01-08)
33 | BJBHT.B6L3 | BLECF_ | 629 | 0x | 0275 | 4 | UJ33 | BY02 | 3 | L | 1 | 8 | B | 15-16 | SR3 | BY05 | C | 2 | 3-4 | BY02 | C | 2 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.03 (09-16) | bar: noise specta 1 to noise specta 3
34 | BJBHT.A6L3 | BLECF_ | 536 | 0x | 0218 | 4 | UJ33 | BY02 | 3 | L | 1 | 7 | B | 13-14 | SR3 | BY05 | C | 2 | 1-2 | BY02 | C | 2 | 6 | 3 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.03 (01-08)
35 | BJBHT.D5L3 | BLECF_ | 175 | 0x | 00AF | 2 | UJ33 | BY02 | 3 | L | 1 | 6 | B | 11-12 | SR3 | BY05 | C | 1 | 11-12 | BY02 | C | 2 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.02 (09-16)
36 | BJBHT.C5L3 | BLECF_ | 577 | 0x | 0241 | 8 | UJ33 | BY02 | 3 | L | 1 | 5 | B | 9-10 | SR3 | BY05 | C | 1 | 9-10 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.01 (09-16)
37 | BJBHT.B5L3 | BLECF_ | 575 | 0x | 023F | 6 | UJ33 | BY02 | 3 | L | 1 | 4 | B | 7-8 | SR3 | BY05 | C | 1 | 7-8 | BY02 | C | 2 | 5 | 2 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.02 (01-08) | bar: noise specta 1 to noise specta 5
38 | BJBHT.A5L3 | BLECF_ | 602 | 0x | 025A | 6 | UJ33 | BY02 | 3 | L | 1 | 3 | B | 5-6 | SR3 | BY05 | C | 1 | 5-6 | BY02 | C | 2 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.01 (09-16)
39 | BJBHT.B4L3 | BLECF_ | 711 | 0x | 02C7 | 2 | UJ33 | BY02 | 3 | L | 1 | 2 | B | 3-4 | SR3 | BY05 | C | 1 | 3-4 | BY02 | C | 2 | 4 | 1 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 0 | [26 empty] | CFV-SR3-BLMC.BLETC.01 (01-08) | bar: noise specta 1 to noise specta 2
40 | BJBHT.A4L3 | BLECF_ | 729 | 0x | 02D9 | 8 | UJ33 | BY02 | 3 | L | 1 | 1 | B | 1-2 | SR3 | BY05 | C | 1 | 1-2 | BY02 | L | 1 | 4 | 1 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLML.BLETC.01 (01-08)
41 | BJBHT.A4R3 | BLECF_ | 543 | 0x | 021F | 8 | UJ33 | BY03 | 3 | R | 1 | 1 | C | 13-14 | SR3 | BY05 | C | 4 | 1-2 | BY02 | R | 3 | 4 | 1 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.01 (01-08)
42 | BJBHT.B4R3 | BLECF_ | 677 | 0x | 02A5 | 2 | UJ33 | BY03 | 3 | R | 1 | 2 | C | 15-16 | SR3 | BY05 | C | 4 | 3-4 | BY02 | C | 2 | 13 | 9 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR3-BLMC.BLETC.09 (01-08) | bar: noise specta 1 to noise specta 2
43 | BJBHT.A5R3 | BLECF_ | 182 | 0x | 00B6 | 6 | UJ33 | BY03 | 3 | R | 1 | 3 | C | 17-18 | SR3 | BY05 | C | 4 | 5-6 | BY02 | C | 2 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.09 (09-16)
44 | BJBHT.B5R3 | BLECF_ | 326 | 0x | 0146 | 6 | UJ33 | BY03 | 3 | R | 1 | 4 | C | 19-20 | SR3 | BY05 | C | 4 | 7-8 | BY02 | C | 2 | 14 | 10 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR3-BLMC.BLETC.10 (01-08) | bar: noise specta 1 to noise specta 5
45 | BJBHT.C5R3 | BLECF_ | 487 | 0x | 01E7 | 8 | UJ33 | BY03 | 3 | R | 1 | 5 | C | 21-22 | SR3 | BY05 | C | 4 | 9-10 | BY02 | R | 3 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1405 | [26 empty] | CFV-SR3-BLMR.BLETC.01 (09-16)
46 | BJBHT.D5R3 | BLECF_ | 393 | 0x | 0189 | 2 | UJ33 | BY03 | 3 | R | 1 | 6 | C | 23-24 | SR3 | BY05 | C | 4 | 11-12 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.10 (09-16) | Cross talk: no action can be done | bar: noise specta 1 to noise specta 2; Modulation 8
47 | BJBHT.A6R3 | BLECF_ | 541 | 0x | 021D | 4 | UJ33 | BY03 | 3 | R | 1 | 7 | D | 1-2 | SR3 | BY05 | C | 5 | 1-2 | BY02 | C | 2 | 15 | 11 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.11 (01-08) | Cross talk: no action can be done | bar: Modulation 8
48 | BJBHT.B6R3 | BLECF_ | 341 | 0x | 0155 | 4 | UJ33 | BY03 | 3 | R | 1 | 8 | D | 3-4 | SR3 | BY05 | C | 5 | 3-4 | BY02 | C | 2 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR3-BLMC.BLETC.11 (09-16) | Cross talk: no action can be done | bar: noise specta 1 to noise specta 4; Modulation 8
49 | BJBHT.C6R3 | BLECF_ | 339 | 0x | 0153 | 6 | UJ33 | BY03 | 3 | R | 1 | 9 | D | 5-6 | SR3 | BY05 | C | 5 | 5-6 | BY02 | R | 3 | 5 | 2 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.02 (01-08) | Cross talk: no action can be done | bar: noise specta 2 to noise specta 6; Modulation 8
0 | BJBHT.A7R3 | BLECF_ | 367 | 0x | 016F | 1 | UJ33 | BY03 | 3 | R | 1 | 10 | D | 7-8 | SR3 | BY05 | C | 5 | 7-8 | BY02 | C | 2 | 16 | 12 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 1321 | [26 empty] | CFV-SR3-BLMC.BLETC.12 (01-08) | Cross talk: no action can be done | bar: noise specta 1; Modulation 2; Modulation 8
51 | BJBHT.B7R3 | BLECF_ | 709 | 0x | 02C5 | 7 | UJ33 | BY03 | 3 | R | 2 | 1 | D | 9-10 | SR3 | BY05 | C | 5 | 9-10 | BY02 | R | 3 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 1321 | [26 empty] | CFV-SR3-BLMR.BLETC.02 (09-16) | Cross talk: no action can be done | bar: Modulation 8
52 | BJBHT.A8R3 | BLECF_ | 502 | 0x | 01F6 | 6 | UJ33 | BY03 | 3 | R | 2 | 2 | D | 11-12 | SR3 | BY05 | C | 5 | 11-12 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.12 (09-16) | Cross talk: no action can be done | bar: Modulation 8
53 | BJBHT.B8R3 | BLECF_ | 183 | 0x | 00B7 | 6 | UJ33 | BY03 | 3 | R | 2 | 3 | D | 13-14 | SR3 | BY05 | C | 6 | 1-2 | BY02 | R | 3 | 6 | 3 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.03 (01-08) | Cross talk: no action can be done | bar: Modulation 8
54 | BJBHT.A9R3 | BLECF_ | 375 | 0x | 0177 | 10 | UJ33 | BY03 | 3 | R | 2 | 4 | D | 15-16 | SR3 | BY05 | C | 6 | 3-4 | BY02 | C | 2 | 17 | 13 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMC.BLETC.13 (01-08)
55 | BJBHT.B9R3 | BLECF_ | 410 | 0x | 019A | 11 | UJ33 | BY03 | 3 | R | 2 | 5 | D | 17-18 | SR3 | BY05 | C | 6 | 5-6 | BY02 | R | 3 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.03 (09-16)
56 | BJBHT.A10R3 | BLECF_ | 480 | 0x | 01E0 | 11 | UJ33 | BY03 | 3 | R | 2 | 6 | D | 19-20 | SR3 | BY05 | C | 6 | 7-8 | BY02 | R | 3 | 7 | 4 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR3-BLMR.BLETC.04 (01-08) | Jonathan and Ion: check in the tunnel necessary (higher amp and 1 missing) | bar: Modulation 3; Modulation 6
57 | BJBHT.A11R3 | BLECF_ | 562 | 0x | 0232 | 12 | UJ33 | BY03 | 3 | R | 2 | 7 | D | 21-22 | SR3 | BY05 | C | 6 | 9-10 | BY02 | C | 2 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1573 | [27 empty] | CFV-SR3-BLMC.BLETC.13 (09-16) | Cross talk: no action can be done | bar: noise specta 2 to noise specta 6; Modulation 8
58 | BJBHT.B11R3 | BLECF_ | 459 | 0x | 01CB | 7 | UJ33 | BY03 | 3 | R | 2 | 8 | D | 23-24 | SR3 | BY05 | C | 6 | 11-12 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.04 (09-16) | Cross talk: no action can be done | bar: noise specta 2 to noise specta 6; Modulation 8
59 | BJBHT.A12R3 | BLECF_ | 472 | 0x | 01D8 | 10 | Arc | BYPLM.A12R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | F | 8 | 7-8 | BY02 | R | 3 | 8 | 5 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR3-BLMR.BLETC.05 (01-08)
60 | BJBHT.A13R3 | BLECF_ | 611 | 0x | 0263 | 10 | Arc | BYPLM.A13R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1418 | [27 empty] | CFV-SR3-BLMR.BLETC.05 (09-16)
61 | BJBHT.A14R3 | BLECF_ | 504 | 0x | 01F8 | 6 | Arc | BYPLM.A14R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | F | 10 | 7-8 | BY02 | R | 3 | 9 | 6 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.06 (01-08)
62 | BJBHT.A15R3 | BLECF_ | 499 | 0x | 01F3 | 6 | Arc | BYPLM.A15R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | F | 11 | 7-8 | BY02 | R | 3 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1404 | [26 empty] | CFV-SR3-BLMR.BLETC.06 (09-16)
63 | BJBHT.A16R3 | BLECF_ | 514 | 0x | 0202 | 6 | Arc | BYPLM.A16R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | F | 12 | 7-8 | BY02 | R | 3 | 10 | 7 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1408 | [27 empty] | CFV-SR3-BLMR.BLETC.07 (01-08)
64 | BJBHT.A17R3 | BLECF_ | 493 | 0x | 01ED | 6 | Arc | BYPLM.A17R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 7 | 7-8 | BY02 | R | 3 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.07 (09-16)
65 | BJBHT.A18R3 | BLECF_ | 496 | 0x | 01F0 | 6 | Arc | BYPLM.A18R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 8 | 7-8 | BY02 | R | 3 | 11 | 8 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.08 (01-08)
66 | BJBHT.A19R3 | BLECF_ | 314 | 0x | 013A | 6 | Arc | BYPLM.A19R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 9 | 7-8 | BY02 | R | 3 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR3-BLMR.BLETC.08 (09-16)
67 | BJBHT.A20R3 | BLECF_ | 523 | 0x | 020B | 6 | Arc | BYPLM.A20R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.09 (01-08) | Jonathan and Ion: check in the tunnel necessary. Exchange of the monitor CH3 | bar: Modulation 5
68 | BJBHT.A21R3 | BLECF_ | 185 | 0x | 00B9 | 6 | Arc | BYPLM.A21R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 0 | [26 empty] | CFV-SR3-BLMR.BLETC.09 (09-16) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 5
69 | BJBHT.A22R3 | BLECF_ | 387 | 0x | 0183 | 6 | Arc | BYPLM.A22R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 12 | 7-8 | BY02 | R | 3 | 14 | 10 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1301 | [27 empty] | CFV-SR3-BLMR.BLETC.10 (01-08)
70 | BJBHT.A23R3 | BLECF_ | 485 | 0x | 01E5 | 6 | Arc | BYPLM.A23R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 7 | 7-8 | BY02 | R | 3 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.10 (09-16)
71 | BJBHT.A24R3 | BLECF_ | 309 | 0x | 0135 | 6 | Arc | BYPLM.A24R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.11 (01-08) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 2; Modulation 6
72 | BJBHT.A25R3 | BLECF_ | 184 | 0x | 00B8 | 6 | Arc | BYPLM.A25R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 9 | 7-8 | BY02 | R | 3 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.11 (09-16)
73 | BJBHT.A26R3 | BLECF_ | 337 | 0x | 0151 | 6 | Arc | BYPLM.A26R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 10 | 7-8 | BY02 | R | 3 | 16 | 12 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.12 (01-08)
74 | BJBHT.A27R3 | BLECF_ | 519 | 0x | 0207 | 6 | Arc | BYPLM.A27R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.12 (09-16) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 5
75 | BJBHT.A28R3 | BLECF_ | 448 | 0x | 01C0 | 6 | Arc | BYPLM.A28R3 | 3 | R |  |  |  | 6-7 | SR3 | BY05 | H | 12 | 6-7 | BY02 | R | 3 | 17 | 13 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 0 | [26 empty] | CFV-SR3-BLMR.BLETC.13 (01-08) | Jonathan and Ion: check in the tunnel necessary Romain and fiber connection 6-7 or 7-8 needs to be verified | bar: Modulation 6
76 | BJBHT.A29R3 | BLECF_ | 489 | 0x | 01E9 | 6 | Arc | BYPLM.A29R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.13 (09-16) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 4; Modulation 6
77 | BJBHT.A30R3 | BLECF_ | 401 | 0x | 0191 | 6 | Arc | BYPLM.A30R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 8 | 7-8 | BY02 | R | 3 | 18 | 14 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.14 (01-08)
78 | BJBHT.A31R3 | BLECF_ | 488 | 0x | 01E8 | 6 | Arc | BYPLM.A31R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 9 | 7-8 | BY02 | R | 3 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1297 | [27 empty] | CFV-SR3-BLMR.BLETC.14 (09-16)
79 | BJBHT.A32R3 | BLECF_ | 407 | 0x | 0197 | 6 | Arc | BYPLM.A32R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 10 | 7-8 | BY02 | R | 3 | 19 | 15 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR3-BLMR.BLETC.15 (01-08)
80 | BJBHT.A33R3 | BLECF_ | 453 | 0x | 01C5 | 6 | Arc | BYPLM.A33R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR3-BLMR.BLETC.15 (09-16) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1
81 | BJBHT.A34R3 | BLECF_ | 109 | 0x | 006D | 6 | Arc | BYPLM.A34R3 | 3 | R |  |  |  | 6-7 | SR3 | BY05 | I | 12 | 6-7 | BY02 | R | 3 | 20 | 16 | 1-8 |  | OK | OK | OK |  |  |  | OK | ↑ | OK | ↑ | ↑ | [8 empty] | 0 | 0 | [26 empty] | CFV-SR3-BLMR.BLETC.16 (01-08) | Romain & Ewald: LF in B fiber connection need to be checked
last entry 19/6/08
| Door | [7 empty] | Transformer soldered
[50 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA
[6 empty] | Card number correct | [43 empty] | noise specta 4: < 100 BLMbits; Modulation 4: o.k.; 10pA 4: o.k.
|  |  |  | 0x | 0000 | Card number needs to be checked
|  |  |  | 0x | 0000 | Card number unknown need to be checked in the tunnel | [43 empty] | noise specta 4: 100-300 BLMbits; Modulation 4: Prob. values mod; 10pA 4: to small values 20s
|  | BLECF_ | 656 | Card was exchanged, Data base need to be checked for the correct number | [45 empty] | noise specta 4: > 300 BLMbits; Modulation 4: Prob. Data base; 10pA 4: Prob. to be checked
[53 empty] | > 522 BLMbits | [7 empty] | Flag missing in DB
[51 empty] | n |  | no data
Note on AQ15: effinger: Ch 5 goes every 20 seconds to 0 all the rest of the time it is working fine, even the runsum 11 is perfect at 1000 BLMbits
Note on BG28: jemery: Seems like monitors are not connected
Note on BH28: jemery: Seems like monitors are not connected
Note on BI28: jemery: Seems like monitors are not connected
Note on BJ28: jemery: Seems like monitors are not connected
Note on BK28: jemery: Seems like monitors are not connected
Note on BL28: jemery: Seems like monitors are not connected
Note on BM28: jemery: Seems like monitors are not connected
Note on BG29: jemery: Seems like monitors are not connected
Note on BH29: jemery: Seems like monitors are not connected
Note on BI29: jemery: Seems like monitors are not connected
Note on BJ29: jemery: Seems like monitors are not connected
Note on BK29: jemery: Seems like monitors are not connected
Note on BL29: jemery: Seems like monitors are not connected
Note on AA30: effinger: CFC card was blocked -> reset done --> o.k. no LF
Note on BG30: jemery: Seems like monitors are not connected
Note on BH30: jemery: Seems like monitors are not connected
Note on BI30: jemery: Seems like monitors are not connected
Note on BJ30: jemery: Seems like monitors are not connected
Note on BK30: jemery: Seems like monitors are not connected
Note on BL30: jemery: Seems like monitors are not connected
Note on BM30: jemery: Seems like monitors are not connected
Note on BN30: jemery: Seems like monitors are not connected
Note on BG33: jemery: Seems like monitors are not connected
Note on BH33: jemery: Seems like monitors are not connected
Note on BI33: jemery: Seems like monitors are not connected
Note on BJ33: jemery: Seems like monitors are not connected
Note on BK33: jemery: Seems like monitors are not connected
Note on BL33: jemery: Seems like monitors are not connected
Note on AM41: effinger: Repaired: rerooting of the cable helped agains the noise
Note on AR41: effinger: Blinking level
Note on AS41: effinger: Blinking level
Note on AT41: effinger: Blinking level
Note on AH48: effinger: LF A Fibre repaired
Note on BN52: jemery: Cross talk?!
Note on BN53: jemery: Cross talk?!
Note on BN54: jemery: Cross talk?!
Note on BN55: jemery: Cross talk?!
Note on BH56: jemery: Cross talk?!
Note on BN56: jemery: Cross talk?!
Note on AA57: effinger: CFC-Card changed because of very low laser power and patch cord changed because of high attenuation
Note on BN57: jemery: Cross talk?!
Note on BN58: jemery: Cross talk?!
Note on BN59: jemery: Cross talk?!
Note on BI62: jemery: To high modulation signal
Note on BL62: jemery: One monitor missing out of 2!
Note on AM63: effinger: Cable will be replace (800m) 14.10.09
Note on BN63: jemery: Cross talk?!
Note on AN64: effinger: Very high DAC value 37x
Note on BN64: jemery: Cross talk?!
Note on BI74: jemery: Higher amplitude and smaller phase. Monitor exchanged and phase correct now
Note on BK74: jemery: Higher amplitude and smaller phase
Note on AI75: effinger: LF fibre problem ! Is repaired
Note on BK75: jemery: Higher amplitude and smaller phase
Note on BH78: jemery: Higher amplitude and smaller phase
Note on BK81: jemery: Higher amplitude and smaller phase
Note on AA82: effinger: in the tunnel with TB o.k. --> Fibre broken tunnel to surface
Note on AH82: effinger: LF a&B fibre repaired
Note on BL82: jemery: Higher amplitude and smaller phase
Note on BJ83: jemery: Higher amplitude and smaller phase
Note on BL83: jemery: Higher amplitude and smaller phase
Note on BG87: jemery: Higher amplitude and smaller phase
Note on AA88: effinger: in the tunnel with TB o.k. --> Fibre broken tunnel to surface
Note on D98: effinger: 565 original number chnaged to 656
Note on BH100: jemery: Spare for phase 2

## Point 4
SX4 | Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | HV Levels | HV Levels | HV Levels | noise specta | [7 empty] | Modulation | [7 empty] | 10pA | [7 empty] | Expert Name
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Scan | Scan | Scan | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | other
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 08.09.09 |  | 13.10.09 |  |  |  | 13.10.09 | [12 empty] | 7.9.09 | 7.9.09 | 9.10.09 | noise specta 1: 10.10 and 12.10; Modulation 1: 8.10 and 12.10 |  | Comments
1 | BJBHT.A33L4 | BLECF_ | 452 | 0x | 01C4 | 6 | Arc | BYPLM.A33L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | I | 5 | 7-8 | BY02 | L | 1 | 19 | 15 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.15 (01-08)
2 | BJBHT.A32L4 | BLECF_ | 748 | 0x | 02EC | 6 | Arc | BYPLM.A32L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | I | 4 | 7-8 | BY02 | L | 1 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.14 (09-16)
3 | BJBHT.A31L4 | BLECF_ | 616 | 0x | 0268 | 6 | Arc | BYPLM.A31L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | I | 3 | 7-8 | BY02 | L | 1 | 18 | 14 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.14 (01-08)
4 | BJBHT.A30L4 | BLECF_ | 662 | 0x | 0296 | 6 | Arc | BYPLM.A30L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | I | 2 | 7-8 | BY02 | L | 1 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.13 (09-16)
5 | BJBHT.A29L4 | BLECF_ | 38 | 0x | 0026 | 6 | Arc | BYPLM.A29L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | I | 1 | 7-8 | BY02 | L | 1 | 17 | 13 | 1-8 |  | OK | ↑ | ↑ | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1336 | 1337 | [24 empty] | CFV-SX4-BLML.BLETC.13 (01-08)
6 | BJBHT.A28L4 | BLECF_ | 76 | 0x | 004C | 6 | Arc | BYPLM.A28L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | H | 6 | 7-8 | BY02 | L | 1 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.12 (09-16) | bar: noise specta 1 to noise specta 6
7 | BJBHT.A27L4 | BLECF_ | 572 | 0x | 023C | 6 | Arc | BYPLM.A27L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | H | 5 | 7-8 | BY02 | L | 1 | 16 | 12 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.12 (01-08)
8 | BJBHT.A26L4 | BLECF_ | 318 | 0x | 013E | 6 | Arc | BYPLM.A26L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.11 (09-16) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 6
9 | BJBHT.A25L4 | BLECF_ | 613 | 0x | 0265 | 6 | Arc | BYPLM.A25L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | H | 3 | 7-8 | BY02 | L | 1 | 15 | 11 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.11 (01-08)
10 | BJBHT.A24L4 | BLECF_ | 655 | 0x | 028F | 6 | Arc | BYPLM.A24L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | H | 2 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [26 empty] | CFV-SX4-BLML.BLETC.10 (09-16)
11 | BJBHT.A23L4 | BLECF_ | 631 | 0x | 0277 | 6 | Arc | BYPLM.A23L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.10 (01-08)
12 | BJBHT.A22L4 | BLECF_ | 743 | 0x | 02E7 | 6 | Arc | BYPLM.A22L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | G | 6 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [26 empty] | CFV-SX4-BLML.BLETC.09 (09-16)
13 | BJBHT.A21L4 | BLECF_ | 664 | 0x | 0298 | 6 | Arc | BYPLM.A21L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 13 | 9 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.09 (01-08)
14 | BJBHT.A20L4 | BLECF_ | 471 | 0x | 01D7 | 6 | Arc | BYPLM.A20L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | G | 4 | 7-8 | BY02 | L | 1 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.08 (09-16)
15 | BJBHT.A19L4 | BLECF_ | 552 | 0x | 0228 | 6 | Arc | BYPLM.A19L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | G | 3 | 7-8 | BY02 | L | 1 | 11 | 8 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.08 (01-08)
16 | BJBHT.A18L4 | BLECF_ | 395 | 0x | 018B | 6 | Arc | BYPLM.A18L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | G | 2 | 7-8 | BY02 | L | 1 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.07 (09-16)
17 | BJBHT.A17L4 | BLECF_ | 615 | 0x | 0267 | 6 | Arc | BYPLM.A17L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | G | 1 | 7-8 | BY02 | L | 1 | 10 | 7 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.07 (01-08)
18 | BJBHT.A16L4 | BLECF_ | 591 | 0x | 024F | 6 | Arc | BYPLM.A16L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | F | 5 | 7-8 | BY02 | L | 1 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.06 (09-16)
19 | BJBHT.A15L4 | BLECF_ | 642 | 0x | 0282 | 6 | Arc | BYPLM.A15L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | F | 4 | 7-8 | BY02 | L | 1 | 9 | 6 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.06 (01-08)
20 | BJBHT.A14L4 | BLECF_ | 670 | 0x | 029E | 6 | Arc | BYPLM.A14L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | F | 3 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.05 (09-16)
21 | BJBHT.A13L4 | BLECF_ | 599 | 0x | 0257 | 6 | Arc | BYPLM.A13L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.05 (01-08)
22 | BJBHT.A12L4 | BLECF_ | 659 | 0x | 0293 | 6 | Arc | BYPLM.A12L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.04 (09-16)
23 | BJBHT.B5L4 |  |  | 0x | 0000 | 0 | UA43 | BY12 | 4 | CL | 1 | 9 | A | 17-18 | SX4 | BY04 | C | 2 | 5-6
24 | BJBHT.A11L4 | BLECF_ | 643 | 0x | 0283 | 6 | UA43 | BY12 | 4 | CL | 1 | 8 | A | 15-16 | SX4 | BY05 | C | 2 | 3-4 | BY02 | L | 1 | 7 | 4 | 1-8 | Fibre missing, check surface TB, PM | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.04 (01-08) | Slava: Expert name missing in MTF | bar: noise specta 6; Modulation 7
25 | BJBHT.A10L4 | BLECF_ | 578 | 0x | 0242 | 6 | UA43 | BY12 | 4 | CL | 1 | 7 | A | 13-14 | SX4 | BY05 | C | 2 | 1-2 | BY02 | L | 1 | 6 | 3 | 9-16 | Fibre missing, check surface TB, PM | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.03 (09-16)
26 | BJBHT.A9L4 | BLECF_ | 408 | 0x | 0198 | 6 | UA43 | BY12 | 4 | CL | 1 | 6 | A | 11-12 | SX4 | BY05 | C | 1 | 11-12 | BY02 | L | 1 | 6 | 3 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.03 (01-08)
27 | BJBHT.A8L4 | BLECF_ | 651 | 0x | 028B | 6 | UA43 | BY12 | 4 | CL | 1 | 5 | A | 9-10 | SX4 | BY05 | C | 1 | 9-10 | BY02 | L | 1 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.02 (09-16)
28 | BJBHT.A7L4 | BLECF_ | 386 | 0x | 0182 | 6 | UA43 | BY12 | 4 | CL | 1 | 4 | A | 7-8 | SX4 | BY05 | C | 1 | 7-8 | BY02 | L | 1 | 5 | 2 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLML.BLETC.02 (01-08)
29 | BJBHT.A6L4 | BLECF_ | 157 | 0x | 009D | 6 | UA43 | BY12 | 4 | CL | 1 | 3 | A | 5-6 | SX4 | BY05 | C | 1 | 5-6 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | ↑ | OK |  |  | OK | ↑ | ↑ | OK | ↑ | [8 empty] | 0 | 1292 | [25 empty] | CFV-SX4-BLML.BLETC.01 (09-16)
30 | BJBHT.C5L4 | BLECF_ | 744 | 0x | 02E8 | 8 | UA43 | BY12 | 4 | CL | 1 | 2 | A | 3-4 | SX4 | BY05 | C | 1 | 3-4 | BY02 | L | 1 | 4 | 1 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1339 | [26 empty] | CFV-SX4-BLML.BLETC.01 (01-08)
31 | BJBHT.B5L4 | BLECF_ | 186 | 0x | 00BA | 2 | UA43 | BY12 | 4 | CL | 1 | 1 | A | 1-2 | SX4 | BY05 | C | 1 | 1-2 | BY02 | C | 2 | 4 | 1 | 1-8 |  | LF | LF | ↑ | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [26 empty] | CFV-SX4-BLMC.BLETC.01 (01-08)
32 | BJBHT.B5R4 | BLECF_ | 8 | 0x | 0008 | 2 | UA47 | BY09 | 4 | CR | 1 | 1 | A | 1-2 | SX4 | BY05 | C | 12 | 1-2 | BY02 | C | 2 | 13 | 9 | 1-8 | wrong C no, check tunnel | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMC.BLETC.09 (01-08)
33 | BJBHT.C5R4 | BLECF_ | 5 | 0x | 0005 | 8 | UA47 | BY09 | 4 | CR | 1 | 2 | A | 3-4 | SX4 | BY05 | C | 12 | 3-4 | BY02 | R | 3 | 4 | 1 | 1-8 | wrong C no, check tunnel | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.01 (01-08)
34 | BJBHT.A6R4 | BLECF_ | 316 | 0x | 013C | 6 | UA47 | BY09 | 4 | CR | 1 | 3 | A | 5-6 | SX4 | BY05 | C | 12 | 5-6 | BY02 | R | 3 | 4 | 1 | 9-16 | no link, check tunnel | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.01 (09-16)
35 | BJBHT.A7R4 | BLECF_ | 556 | 0x | 022C | 6 | UA47 | BY09 | 4 | CR | 1 | 4 | A | 7-8 | SX4 | BY05 | C | 12 | 7-8 | BY02 | R | 3 | 5 | 2 | 1-8 | no link, check tunnel | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.02 (01-08)
36 | BJBHT.A8R4 | BLECF_ | 584 | 0x | 0248 | 6 | UA47 | BY09 | 4 | CR | 1 | 5 | A | 9-10 | SX4 | BY05 | C | 12 | 9-10 | BY02 | R | 3 | 5 | 2 | 9-16 | no link, check tunnel | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.02 (09-16)
37 | BJBHT.A9R4 | BLECF_ | 509 | 0x | 01FD | 6 | UA47 | BY09 | 4 | CR | 1 | 6 | A | 11-12 | SX4 | BY05 | C | 12 | 11-12 | BY02 | R | 3 | 6 | 3 | 1-8 | no link, check tunnel | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.03 (01-08)
38 | BJBHT.A10R4 | BLECF_ | 7 | 0x | 0007 | 6 | UA47 | BY09 | 4 | CR | 1 | 7 | A | 13-14 | SX4 | BY05 | C | 11 | 1-2 | BY02 | R | 3 | 6 | 3 | 9-16 | wrong C no, check tunnel | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.03 (09-16)
39 | BJBHT.A11R4 | BLECF_ | 10 | 0x | 000A | 6 | UA47 | BY09 | 4 | CR | 1 | 8 | A | 15-16 | SX4 | BY05 | C | 11 | 3-4 | BY02 | R | 3 | 7 | 4 | 1-8 | wrong C no, check tunnel | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1399 | [26 empty] | CFV-SX4-BLMR.BLETC.04 (01-08) | Slava: Expert name missing in MTF | bar: Modulation 7
40 | BJBHT.A5R4 |  |  | 0x | 0000 | 0 | UA47 | BY09 | 4 | CR | 1 | 9 | A | 17-18 | SX4 | BY05 | C | 11 | 5-6
41 | BJBHT.A12R4 | BLECF_ | 217 | 0x | 00D9 | 6 | Arc | BYPLM.A12R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | F | 8 | 7-8 | BY02 | R | 3 | 7 | 4 | 9-16 | Fibre missing, check surface TB, PM | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.04 (09-16)
42 | BJBHT.A13R4 | BLECF_ | 531 | 0x | 0213 | 6 | Arc | BYPLM.A13R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 8 | 5 | 1-8 | Fibre missing, check surface TB, PM | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.05 (01-08)
43 | BJBHT.A14R4 | BLECF_ | 568 | 0x | 0238 | 6 | Arc | BYPLM.A14R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | F | 10 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 | Fibre missing, check surface TB, PM | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.05 (09-16)
44 | BJBHT.A15R4 | BLECF_ | 57 | 0x | 0039 | 6 | Arc | BYPLM.A15R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | F | 11 | 7-8 | BY02 | R | 3 | 9 | 6 | 1-8 | Fibre missing, check surface TB, PM | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.06 (01-08) | bar: noise specta 1 to noise specta 6
45 | BJBHT.A16R4 | BLECF_ | 644 | 0x | 0284 | 6 | Arc | BYPLM.A16R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | F | 12 | 7-8 | BY02 | R | 3 | 9 | 6 | 9-16 | Fibre missing, check surface TB, PM | LF | LF | OK | OK |  |  | OK | OK | OK | OK | OK | [10 empty] | 0 | [24 empty] | CFV-SX4-BLMR.BLETC.06 (09-16)
46 | BJBHT.A17R4 | BLECF_ | 403 | 0x | 0193 | 6 | Arc | BYPLM.A17R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | G | 7 | 7-8 | BY02 | R | 3 | 10 | 7 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.07 (01-08)
47 | BJBHT.A18R4 | BLECF_ | 558 | 0x | 022E | 6 | Arc | BYPLM.A18R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | G | 8 | 7-8 | BY02 | R | 3 | 10 | 7 | 9-16 | Card o.k. | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.07 (09-16)
48 | BJBHT.A19R4 | BLECF_ | 199 | 0x | 00C7 | 6 | Arc | BYPLM.A19R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | G | 9 | 7-8 | BY02 | R | 3 | 11 | 8 | 1-8 | Card didn't work, reset than o.k. | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.08 (01-08)
49 | BJBHT.A20R4 | BLECF_ | 585 | 0x | 0249 | 6 | Arc | BYPLM.A20R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.08 (09-16)
50 | BJBHT.A21R4 | BLECF_ | 315 | 0x | 013B | 6 | Arc | BYPLM.A21R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.09 (01-08)
51 | BJBHT.A22R4 | BLECF_ | 340 | 0x | 0154 | 6 | Arc | BYPLM.A22R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | G | 12 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.09 (09-16)
52 | BJBHT.A23R4 | BLECF_ | 537 | 0x | 0219 | 6 | Arc | BYPLM.A23R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | H | 7 | 7-8 | BY02 | R | 3 | 14 | 10 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.10 (01-08)
53 | BJBHT.A24R4 | BLECF_ | 405 | 0x | 0195 | 6 | Arc | BYPLM.A24R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.10 (09-16)
54 | BJBHT.A25R4 | BLECF_ | 483 | 0x | 01E3 | 6 | Arc | BYPLM.A25R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | H | 9 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.11 (01-08)
55 | BJBHT.A26R4 | BLECF_ | 438 | 0x | 01B6 | 6 | Arc | BYPLM.A26R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | H | 10 | 7-8 | BY02 | R | 3 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.11 (09-16)
56 | BJBHT.A27R4 | BLECF_ | 547 | 0x | 0223 | 6 | Arc | BYPLM.A27R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 1-8 | Card didn't work, reset than o.k. | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.12 (01-08)
57 | BJBHT.A28R4 | BLECF_ | 551 | 0x | 0227 | 6 | Arc | BYPLM.A28R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | H | 12 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.12 (09-16)
58 | BJBHT.A29R4 | BLECF_ | 83 | 0x | 0053 | 6 | Arc | BYPLM.A29R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.13 (01-08)
59 | BJBHT.A30R4 | BLECF_ | 435 | 0x | 01B3 | 6 | Arc | BYPLM.A30R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | I | 8 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.13 (09-16)
60 | BJBHT.A31R4 | BLECF_ | 40 | 0x | 0028 | 6 | Arc | BYPLM.A31R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | I | 9 | 7-8 | BY02 | R | 3 | 18 | 14 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.14 (01-08) | bar: noise specta 1 to noise specta 6
61 | BJBHT.A32R4 | BLECF_ | 192 | 0x | 00C0 | 6 | Arc | BYPLM.A32R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | I | 10 | 7-8 | BY02 | R | 3 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.14 (09-16)
62 | BJBHT.A33R4 | BLECF_ | 582 | 0x | 0246 | 6 | Arc | BYPLM.A33R4 | 4 | R |  |  |  | 7-8 | SX4 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.15 (01-08)
63 | BJBHT.A34R4 | BLECF_ | 389 | 0x | 0185 | 6 | Arc | BYPLM.A34R4 | 4 | R |  |  |  | 7-9 | SX4 | BY05 | I | 12 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SX4-BLMR.BLETC.15 (09-16)
last entry 16/7/08
Transformer soldered
[49 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA
[6 empty] | Card number correct | [42 empty] | noise specta 4: < 100 BLMbits; Modulation 4: o.k.; 10pA 4: o.k.
|  |  |  | 0x | 0000 | Card number needs to be checked
|  |  |  | 0x | 0000 | Card number unknown need to be checked in the tunnel | [42 empty] | noise specta 4: 100-300 BLMbits; Modulation 4: Prob. values mod; 10pA 4: to small values 20s
|  | BLECF_ | 656 | Card was exchanged, Data base need to be checked for the correct number | [44 empty] | noise specta 4: > 300 BLMbits; Modulation 4: Prob. Data base; 10pA 4: Prob. to be checked
[52 empty] | > 522 BLMbits | [7 empty] | Flag missing in DB
[50 empty] | n |  | no data
Note on AV3: effinger: Repaired week 31 scan necessary to verify
Note on AW3: effinger: Scan 12.10.09 same result -> one card is not working -> FPGA reset
Note on BK12: jemery: Higher amplitude
Note on AH16: effinger: LF a&B while last check 8.9.09
Note on BL29: jemery: Monitor missing in MTF
Note on AI31: effinger: LF while check 8.9.09
Note on AA38: effinger: Patch pannel C12 and C11 inversed -> we exchanged patch cords -> no it is o.k.
Note on BL45: jemery: Monitor missing in MTF
Note on AA48: effinger: Card didn't work, reset than o.k.
Note on AA52: effinger: Card No. wrong -> reset -> o.k.
Note on D80: effinger: 565 original number chnaged to 656
Note on BG82: jemery: Spare for phase 2

## Point 5
SR5 | Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | HV Levels | HV Levels | HV Levels | noise specta | [7 empty] | Modulation | [7 empty] | 10pA | [7 empty] | Expert Name
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Scan | Scan | Scan | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | other
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 08.09.09 |  | 13.10.09 |  |  |  | 13.10.09 | [12 empty] | 31.8.09 | 2.10.09 | 9.10.09 | noise specta 1: 10.10 and 12.10; Modulation 1: 8.10 and 12.10 |  | Comments
1 | BJBHT.A33L5 | BLECF_ | 335 | 0x | 014F | 6 | Arc | BYPLM.A33L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | I | 5 | 7-8 | BY02 | L | 1 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.15 (09-16)
2 | BJBHT.A32L5 | BLECF_ | 330 | 0x | 014A | 6 | Arc | BYPLM.A32L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | I | 4 | 7-8 | BY02 | L | 1 | 19 | 15 | 1-8 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.15 (01-08)
3 | BJBHT.A31L5 | BLECF_ | 650 | 0x | 028A | 6 | Arc | BYPLM.A31L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | I | 3 | 7-8 | BY02 | L | 1 | 18 | 14 | 9-16 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.14 (09-16)
4 | BJBHT.A30L5 | BLECF_ | 414 | 0x | 019E | 6 | Arc | BYPLM.A30L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | I | 2 | 7-8 | BY02 | L | 1 | 18 | 14 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.14 (01-08)
5 | BJBHT.A29L5 | BLECF_ | 307 | 0x | 0133 | 6 | Arc | BYPLM.A29L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | I | 1 | 7-8 | BY02 | L | 1 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.13 (09-16)
6 | BJBHT.A28L5 | BLECF_ | 447 | 0x | 01BF | 6 | Arc | BYPLM.A28L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | H | 6 | 7-8 | BY02 | L | 1 | 17 | 13 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.13 (01-08)
7 | BJBHT.A27L5 | BLECF_ | 226 | 0x | 00E2 | 6 | Arc | BYPLM.A27L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | H | 5 | 7-8 | BY02 | L | 1 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.12 (09-16)
8 | BJBHT.A26L5 | BLECF_ | 680 | 0x | 02A8 | 6 | Arc | BYPLM.A26L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 16 | 12 | 1-8 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.12 (01-08)
9 | BJBHT.A25L5 | BLECF_ | 424 | 0x | 01A8 | 6 | Arc | BYPLM.A25L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | H | 3 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.11 (09-16)
10 | BJBHT.A24L5 | BLECF_ | 419 | 0x | 01A3 | 6 | Arc | BYPLM.A24L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | H | 2 | 7-8 | BY02 | L | 1 | 15 | 11 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.11 (01-08)
11 | BJBHT.A23L5 | BLECF_ | 42 | 0x | 002A | 6 | Arc | BYPLM.A23L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.10 (09-16) | bar: noise specta 1 to noise specta 6
12 | BJBHT.A22L5 | BLECF_ | 625 | 0x | 0271 | 6 | Arc | BYPLM.A22L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | G | 6 | 7-8 | BY02 | L | 1 | 14 | 10 | 1-8 | Test in tunnel needed! | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.10 (01-08)
13 | BJBHT.A21L5 | BLECF_ | 506 | 0x | 01FA | 6 | Arc | BYPLM.A21L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.09 (09-16)
14 | BJBHT.A20L5 | BLECF_ | 589 | 0x | 024D | 6 | Arc | BYPLM.A20L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | G | 4 | 7-8 | BY02 | L | 1 | 13 | 9 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.09 (01-08)
15 | BJBHT.A19L5 | BLECF_ | 546 | 0x | 0222 | 6 | Arc | BYPLM.A19L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | G | 3 | 7-8 | BY02 | L | 1 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.08 (09-16) | bar: noise specta 6
16 | BJBHT.A18L5 | BLECF_ | 473 | 0x | 01D9 | 6 | Arc | BYPLM.A18L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | G | 2 | 7-8 | BY02 | L | 1 | 11 | 8 | 1-8 | Test in tunnel needed! | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.08 (01-08)
17 | BJBHT.A17L5 | BLECF_ | 475 | 0x | 01DB | 6 | Arc | BYPLM.A17L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | G | 1 | 7-8 | BY02 | L | 1 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.07 (09-16)
18 | BJBHT.A16L5 | BLECF_ | 196 | 0x | 00C4 | 6 | Arc | BYPLM.A16L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | F | 5 | 7-8 | BY02 | L | 1 | 10 | 7 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.07 (01-08)
19 | BJBHT.A15L5 | BLECF_ | 346 | 0x | 015A | 6 | Arc | BYPLM.A15L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | F | 4 | 7-8 | BY02 | L | 1 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.06 (09-16) | bar: noise specta 6
20 | BJBHT.A14L5 | BLECF_ | 48 | 0x | 0030 | 6 | Arc | BYPLM.A14L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | F | 3 | 7-8 | BY02 | L | 1 | 9 | 6 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.06 (01-08) | bar: noise specta 2 to noise specta 6
21 | BJBHT.A13L5 | BLECF_ | 640 | 0x | 0280 | 6 | Arc | BYPLM.A13L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.05 (09-16) | Slava: Expert name missing in MTF | bar: Modulation 8
22 | BJBHT.A12L5 | BLECF_ | 477 | 0x | 01DD | 6 | Arc | BYPLM.A12L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.05 (01-08)
23 | BJBHT.B11L5 | BLECF_ | 753 | 0x | 02F1 | 6 | RR53 | BY02 | 5 | CL | 2 | 9 | B | 13-14 | SR5 | BY05 | C | 4 | 1-2 | BY02 | L | 1 | 7 | 4 | 9-16 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.04 (09-16) | bar: noise specta 1 to noise specta 6
24 | BJBHT.A11L5 | BLECF_ | 581 | 0x | 0245 | 7 | RR53 | BY02 | 5 | CL | 2 | 8 | B | 11-12 | SR5 | BY05 | C | 3 | 11-12 | BY02 | C | 2 | 9 | 6 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.06 (01-08) | bar: noise specta 1; noise specta 3 to noise specta 6
25 | BJBHT.B10L5 | BLECF_ | 14 | 0x | 000E | 6 | RR53 | BY02 | 5 | CL | 2 | 7 | B | 9-10 | SR5 | BY05 | C | 3 | 9-10 | BY02 | L | 1 | 7 | 4 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | ↑ | OK | ↑ | [35 empty] | CFV-SR5-BLML.BLETC.04 (01-08) | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: noise specta 2; Modulation 2
26 | BJBHT.A10L5 | BLECF_ | 124 | 0x | 007C | 2 | RR53 | BY02 | 5 | CL | 2 | 6 | B | 7-8 | SR5 | BY05 | C | 3 | 7-8 | BY02 | C | 2 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.05 (09-16)
27 | BJBHT.A9L5 | BLECF_ | 757 | 0x | 02F5 | 6 | RR53 | BY02 | 5 | CL | 2 | 5 | B | 5-6 | SR5 | BY05 | C | 3 | 5-6 | BY02 | L | 1 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [10 empty] | 1320 | [24 empty] | CFV-SR5-BLML.BLETC.03 (09-16) | bar: noise specta 3 to noise specta 4
28 | BJBHT.B8L5 | BLECF_ | 190 | 0x | 00BE | 6 | RR53 | BY02 | 5 | CL | 2 | 4 | B | 3-4 | SR5 | BY05 | C | 3 | 3-4 | BY02 | L | 1 | 6 | 3 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.03 (01-08)
29 | BJBHT.A8L5 | BLECF_ | 9 | 0x | 0009 | 6 | RR53 | BY02 | 5 | CL | 2 | 3 | B | 1-2 | SR5 | BY05 | C | 3 | 1-2 | BY02 | C | 2 | 8 | 5 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.05 (01-08)
30 | BJBHT.A7L5 | BLECF_ | 525 | 0x | 020D | 6 | RR53 | BY02 | 5 | CL | 2 | 2 | A | 23-24 | SR5 | BY05 | C | 2 | 11-12 | BY02 | L | 1 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.02 (09-16)
31 | BJBHT.B6L5 | BLECF_ | 632 | 0x | 0278 | 7 | RR53 | BY02 | 5 | CL | 2 | 1 | A | 21-22 | SR5 | BY05 | C | 2 | 9-10 | BY02 | L | 1 | 5 | 2 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.02 (01-08)
32 | BJBHT.A6L5 | BLECF_ | 103 | 0x | 0067 | 1 | RR53 | BY02 | 5 | CL | 1 | 10 | A | 19-20 | SR5 | BY05 | C | 2 | 7-8 | BY02 | C | 2 | 7 | 4 | 9-16 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.04 (09-16)
33 | BJBHT.B5L5 | BLECF_ | 313 | 0x | 0139 | 6 | RR53 | BY02 | 5 | CL | 1 | 9 | A | 17-18 | SR5 | BY05 | C | 2 | 5-6 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.01 (09-16)
34 | BJBHT.A5L5 | BLECF_ | 521 | 0x | 0209 | 2 | RR53 | BY02 | 5 | CL | 1 | 8 | A | 15-16 | SR5 | BY05 | C | 2 | 3-4 | BY02 | C | 2 | 7 | 4 | 1-8 |  | ↑ | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.04 (01-08) | bar: noise specta 1
35 | BJBHT.C4L5 | BLECF_ | 356 | 0x | 0164 | 6 | RR53 | BY02 | 5 | CL | 1 | 7 | A | 13-14 | SR5 | BY05 | C | 2 | 1-2 | BY02 | L | 1 | 4 | 1 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLML.BLETC.01 (01-08) | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 1
36 | BJBHT.B4L5 | BLECF_ | 370 | 0x | 0172 | 7 | RR53 | BY02 | 5 | CL | 1 | 6 | A | 11-12 | SR5 | BY05 | C | 1 | 11-12 | BY02 | C | 2 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.03 (09-16) | bar: noise specta 1 to noise specta 4
37 | BJBHT.A4L5 | BLECF_ | 3 | 0x | 0003 | 2 | RR53 | BY02 | 5 | CL | 1 | 5 | A | 9-10 | SR5 | BY05 | C | 1 | 9-10 | BY02 | C | 2 | 6 | 3 | 1-8 |  | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.03 (01-08)
38 | BJBHT.A3L5 | BLECF_ | 121 | 0x | 0079 | 5 | RR53 | BY02 | 5 | CL | 1 | 4 | A | 7-8 | SR5 | BY05 | C | 1 | 7-8 | BY02 | C | 2 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.02 (09-16)
39 | BJBHT.A2L5 | BLECF_ | 312 | 0x | 0138 | 8 | RR53 | BY02 | 5 | CL | 1 | 3 | A | 5-6 | SR5 | BY05 | C | 1 | 5-6 | BY02 | C | 2 | 5 | 2 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.02 (01-08)
40 | BJBHT.B1L5 | BLECF_ | 586 | 0x | 024A | 4 | RR53 | BY02 | 5 | CL | 1 | 2 | A | 3-4 | SR5 | BY05 | C | 1 | 3-4 | BY02 | C | 2 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.01 (09-16)
41 | BJBHT.A1L5 | BLECF_ | 579 | 0x | 0243 | 2 | RR53 | BY02 | 5 | CL | 1 | 1 | A | 1-2 | SR5 | BY05 | C | 1 | 1-2 | BY02 | C | 2 | 4 | 1 | 1-8 |  | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.01 (01-08) | bar: noise specta 1
42 | BJBHT.A1R5 | BLECF_ | 193 | 0x | 00C1 | 2 | RR57 | BY02 | 5 | CR | 1 | 1 | A | 1-2 | SR5 | BY05 | C | 12 | 1-2 | BY02 | C | 2 | 13 | 9 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.09 (01-08) | bar: noise specta 1
43 | BJBHT.B1R5 | BLECF_ | 749 | 0x | 02ED | 6 | RR57 | BY02 | 5 | CR | 1 | 2 | A | 3-4 | SR5 | BY05 | C | 12 | 3-4 | BY02 | C | 2 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.09 (09-16)
44 | BJBHT.A2R5 | BLECF_ | 671 | 0x | 029F | 6 | RR57 | BY02 | 5 | CR | 1 | 3 | A | 5-6 | SR5 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.10 (01-08)
45 | BJBHT.A3R5 | BLECF_ | 750 | 0x | 02EE | 6 | RR57 | BY02 | 5 | CR | 1 | 4 | A | 7-8 | SR5 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.10 (09-16)
46 | BJBHT.A4R5 | BLECF_ | 726 | 0x | 02D6 | 2 | RR57 | BY02 | 5 | CR | 1 | 5 | A | 9-10 | SR5 | BY05 | C | 12 | 9-10 | BY02 | C | 2 | 15 | 11 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.11 (01-08)
47 | BJBHT.B4R5 | BLECF_ | 663 | 0x | 0297 | 8 | RR57 | BY02 | 5 | CR | 1 | 6 | A | 11-12 | SR5 | BY05 | C | 12 | 11-12 | BY02 | C | 2 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.11 (09-16) | bar: noise specta 1 to noise specta 4
48 | BJBHT.C4R5 | BLECF_ | 710 | 0x | 02C6 | 6 | RR57 | BY02 | 5 | CR | 1 | 7 | A | 13-14 | SR5 | BY05 | C | 11 | 1-2 | BY02 | R | 3 | 4 | 1 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.01 (01-08)
49 | BJBHT.A5R5 | BLECF_ | 598 | 0x | 0256 | 2 | RR57 | BY02 | 5 | CR | 1 | 8 | A | 15-16 | SR5 | BY05 | C | 11 | 3-4 | BY02 | C | 2 | 16 | 12 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.12 (01-08) | bar: noise specta 1
50 | BJBHT.B5R5 | BLECF_ | 697 | 0x | 02B9 | 6 | RR57 | BY02 | 5 | CR | 1 | 9 | A | 17-18 | SR5 | BY05 | C | 11 | 5-6 | BY02 | R | 3 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.01 (09-16)
51 | BJBHT.A6R5 | BLECF_ | 648 | 0x | 0288 | 2 | RR57 | BY02 | 5 | CR | 1 | 10 | A | 19-20 | SR5 | BY05 | C | 11 | 7-8 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.12 (09-16)
52 | BJBHT.B6R5 | BLECF_ | 565 | 0x | 0235 | 6 | RR57 | BY02 | 5 | CR | 2 | 1 | A | 21-22 | SR5 | BY05 | C | 11 | 9-10 | BY02 | R | 3 | 5 | 2 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.02 (01-08)
53 | BJBHT.A7R5 | BLECF_ | 618 | 0x | 026A | 6 | RR57 | BY02 | 5 | CR | 2 | 2 | A | 23-24 | SR5 | BY05 | C | 11 | 11-12 | BY02 | R | 3 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.02 (09-16)
54 | BJBHT.A8R5 | BLECF_ | 596 | 0x | 0254 | 6 | RR57 | BY02 | 5 | CR | 2 | 3 | B | 1-2 | SR5 | BY05 | C | 10 | 1-2 | BY02 | C | 2 | 17 | 13 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.13 (01-08)
55 | BJBHT.B8R5 | BLECF_ | 660 | 0x | 0294 | 6 | RR57 | BY02 | 5 | CR | 2 | 4 | B | 3-4 | SR5 | BY05 | C | 10 | 3-4 | BY02 | R | 3 | 6 | 3 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.03 (01-08)
56 | BJBHT.A9R5 | BLECF_ | 149 | 0x | 0095 | 6 | RR57 | BY02 | 5 | CR | 2 | 5 | B | 5-6 | SR5 | BY05 | C | 10 | 5-6 | BY02 | R | 3 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.03 (09-16)
57 | BJBHT.A10R5 | BLECF_ | 605 | 0x | 025D | 2 | RR57 | BY02 | 5 | CR | 2 | 6 | B | 7-8 | SR5 | BY05 | C | 10 | 7-8 | BY02 | C | 2 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.13 (09-16)
58 | BJBHT.B10R5 | BLECF_ | 673 | 0x | 02A1 | 6 | RR57 | BY02 | 5 | CR | 2 | 7 | B | 9-10 | SR5 | BY05 | C | 10 | 9-10 | BY02 | R | 3 | 7 | 4 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.04 (01-08)
59 | BJBHT.A11R5 | BLECF_ | 621 | 0x | 026D | 8 | RR57 | BY02 | 5 | CR | 2 | 8 | B | 11-12 | SR5 | BY05 | C | 10 | 11-12 | BY02 | C | 2 | 18 | 14 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMC.BLETC.14 (01-08)
60 | BJBHT.B11R5 | BLECF_ | 603 | 0x | 025B | 6 | RR57 | BY02 | 5 | CR | 2 | 9 | B | 13-14 | SR5 | BY05 | C | 9 | 1-2 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.04 (09-16) | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 7 to Modulation 8
61 | BJBHT.A12R5 | BLECF_ | 699 | 0x | 02BB | 6 | Arc | BYPLM.A12R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | F | 8 | 7-8 | BY02 | R | 3 | 8 | 5 | 1-8 | Test in tunnel needed! | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.05 (01-08)
62 | BJBHT.A13R5 | BLECF_ | 728 | 0x | 02D8 | 6 | Arc | BYPLM.A13R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.05 (09-16) | Slava: Expert name missing in MTF | bar: Modulation 7
63 | BJBHT.A14R5 | BLECF_ | 698 | 0x | 02BA | 6 | Arc | BYPLM.A14R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | F | 10 | 7-8 | BY02 | R | 3 | 9 | 6 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.06 (01-08)
64 | BJBHT.A15R5 | BLECF_ | 737 | 0x | 02E1 | 6 | Arc | BYPLM.A15R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | F | 11 | 7-8 | BY02 | R | 3 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.06 (09-16)
65 | BJBHT.A16R5 | BLECF_ | 733 | 0x | 02DD | 6 | Arc | BYPLM.A16R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | F | 12 | 7-8 | BY02 | R | 3 | 10 | 7 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.07 (01-08)
66 | BJBHT.A17R5 | BLECF_ | 634 | 0x | 027A | 6 | Arc | BYPLM.A17R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | G | 7 | 7-8 | BY02 | R | 3 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.07 (09-16)
67 | BJBHT.A18R5 | BLECF_ | 732 | 0x | 02DC | 6 | Arc | BYPLM.A18R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | G | 8 | 7-8 | BY02 | R | 3 | 11 | 8 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.08 (01-08)
68 | BJBHT.A19R5 | BLECF_ | 742 | 0x | 02E6 | 6 | Arc | BYPLM.A19R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | G | 9 | 7-8 | BY02 | R | 3 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.08 (09-16)
69 | BJBHT.A20R5 | BLECF_ | 695 | 0x | 02B7 | 6 | Arc | BYPLM.A20R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.09 (01-08)
70 | BJBHT.A21R5 | BLECF_ | 688 | 0x | 02B0 | 6 | Arc | BYPLM.A21R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.09 (09-16)
71 | BJBHT.A22R5 | BLECF_ | 739 | 0x | 02E3 | 6 | Arc | BYPLM.A22R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | G | 12 | 7-8 | BY02 | R | 3 | 14 | 10 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.10 (01-08)
72 | BJBHT.A23R5 | BLECF_ | 691 | 0x | 02B3 | 6 | Arc | BYPLM.A23R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | H | 7 | 7-8 | BY02 | R | 3 | 14 | 10 | 9-16 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.10 (09-16)
73 | BJBHT.A24R5 | BLECF_ | 617 | 0x | 0269 | 6 | Arc | BYPLM.A24R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.11 (01-08)
74 | BJBHT.A25R5 | BLECF_ | 736 | 0x | 02E0 | 6 | Arc | BYPLM.A25R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | H | 9 | 7-8 | BY02 | R | 3 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.11 (09-16)
75 | BJBHT.A26R5 | BLECF_ | 683 | 0x | 02AB | 6 | Arc | BYPLM.A26R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | H | 10 | 7-8 | BY02 | R | 3 | 16 | 12 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.12 (01-08)
76 | BJBHT.A27R5 | BLECF_ | 490 | 0x | 01EA | 6 | Arc | BYPLM.A27R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.12 (09-16)
77 | BJBHT.A28R5 | BLECF_ | 734 | 0x | 02DE | 6 | Arc | BYPLM.A28R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | H | 12 | 7-8 | BY02 | R | 3 | 17 | 13 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.13 (01-08)
78 | BJBHT.A29R5 | BLECF_ | 701 | 0x | 02BD | 6 | Arc | BYPLM.A29R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.13 (09-16)
79 | BJBHT.A30R5 | BLECF_ | 704 | 0x | 02C0 | 6 | Arc | BYPLM.A30R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | I | 8 | 7-8 | BY02 | R | 3 | 18 | 14 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.14 (01-08)
80 | BJBHT.A31R5 | BLECF_ | 693 | 0x | 02B5 | 6 | Arc | BYPLM.A31R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | I | 9 | 7-8 | BY02 | R | 3 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.14 (09-16)
81 | BJBHT.A32R5 | BLECF_ | 735 | 0x | 02DF | 6 | Arc | BYPLM.A32R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | I | 10 | 7-8 | BY02 | R | 3 | 19 | 15 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.15 (01-08)
82 | BJBHT.A33R5 | BLECF_ | 731 | 0x | 02DB | 6 | Arc | BYPLM.A33R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.15 (09-16)
83 | BJBHT.A34R5 | BLECF_ | 661 | 0x | 0295 | 6 | Arc | BYPLM.A34R5 | 5 | R |  |  |  | 7-9 | SR5 | BY05 | I | 12 | 7-8 | BY02 | R | 3 | 20 | 16 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [35 empty] | CFV-SR5-BLMR.BLETC.16 (01-08)
last entry 22/5/08
| Door | [7 empty] | Transformer soldered
[49 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA
[6 empty] | Card number correct | [42 empty] | noise specta 4: < 100 BLMbits; Modulation 4: o.k.; 10pA 4: o.k.
|  |  |  | 0x | 0000 | Card number needs to be checked
|  |  |  | 0x | 0000 | Card number unknown need to be checked in the tunnel | [42 empty] | noise specta 4: 100-300 BLMbits; Modulation 4: Prob. values mod; 10pA 4: to small values 20s
|  | BLECF_ | 656 | Card was exchanged, Data base need to be checked for the correct number | [44 empty] | noise specta 4: > 300 BLMbits; Modulation 4: Prob. Data base; 10pA 4: Prob. to be checked
[52 empty] | > 522 BLMbits | [7 empty] | Flag missing in DB
[50 empty] | n |  | no data
Note on AU3: effinger: Scan 16.09.09 still all o.k
Note on AV3: effinger: Scan 16.09.09 still all o.k
Note on BM25: jemery: Unconnected monitor
Note on BG30: jemery: Lower phase
Note on BF40: jemery: Strange signal. Different amplitude and phase
Note on BL66: jemery: Missing expert name
Note on BM66: jemery: Expert name exist, but should be in ch 15
Note on AA68: effinger: both jumper not correctly pluged, Card o.k.,
Note on BL69: jemery: Missing monitor
Note on AA76: effinger: jumper not correctly pluged, Card o.k.,
Note on AA79: effinger: jumper not correctly pluged, Card o.k.,
Note on AH81: effinger: Card did not work after reset (28.9.09) new reset done on the 29.9.09 than card is working
Note on AI81: effinger: Card did not work after reset (28.9.09) new reset done on the 29.9.09 than card is working
Note on D100: effinger: 565 original number chnaged to 656
Note on BG102: jemery: Spare for phase 2

## Point 6
SR6 | Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | HV Levels | HV Levels | HV Levels | HV Levels | noise specta | [7 empty] | Modulation | [7 empty] | 10pA | [7 empty] | Expert Name
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Scan | Scan | Scan | Scan | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | other
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 23.09.09 |  | 13.10.09 |  |  |  | 13.10.09 | [12 empty] | 7.9.09 | 23.9.09 | 2.10.09 | 9.10.09 | noise specta 1: 10.10 and 12.10; Modulation 1: 8.10 and 12.10 |  | Comments
1 | BJBHT.A33L6 | BLECF_ | 533 | 0x | 0215 | 6 | Arc | BYPLM.A33L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | I | 5 | 7-8 | BY02 | L | 1 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.14 (09-16)
2 | BJBHT.A32L6 | BLECF_ | 117 | 0x | 0075 | 6 | Arc | BYPLM.A32L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | I | 4 | 7-8 | BY02 | L | 1 | 18 | 14 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.14 (01-08)
3 | BJBHT.A31L6 | BLECF_ | 232 | 0x | 00E8 | 6 | Arc | BYPLM.A31L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | I | 3 | 7-8 | BY02 | L | 1 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.13 (09-16)
4 | BJBHT.A30L6 | BLECF_ | 93 | 0x | 005D | 6 | Arc | BYPLM.A30L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | I | 2 | 7-8 | BY02 | L | 1 | 17 | 13 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1406 | [27 empty] | CFV-SR6-BLML.BLETC.13 (01-08) | bar: noise specta 6
5 | BJBHT.A29L6 | BLECF_ | 163 | 0x | 00A3 | 6 | Arc | BYPLM.A29L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | I | 1 | 7-8 | BY02 | L | 1 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR6-BLML.BLETC.12 (09-16)
6 | BJBHT.A28L6 | BLECF_ | 549 | 0x | 0225 | 6 | Arc | BYPLM.A28L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | H | 6 | 7-8 | BY02 | L | 1 | 16 | 12 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.12 (01-08)
7 | BJBHT.A27L6 | BLECF_ | 166 | 0x | 00A6 | 6 | Arc | BYPLM.A27L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | H | 5 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 |  | up not o.k down o.k | [25 empty] | CFV-SR6-BLML.BLETC.11 (09-16)
8 | BJBHT.A26L6 | BLECF_ | 266 | 0x | 010A | 6 | Arc | BYPLM.A26L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 15 | 11 | 1-8 |  | OK | ↑ | ↑ | OK |  |  | OK | OK | ↑ | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.11 (01-08) | bar: noise specta 3 to noise specta 6
9 | BJBHT.A25L6 | BLECF_ | 162 | 0x | 00A2 | 6 | Arc | BYPLM.A25L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | H | 3 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.10 (09-16)
10 | BJBHT.A24L6 | BLECF_ | 168 | 0x | 00A8 | 6 | Arc | BYPLM.A24L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | H | 2 | 7-8 | BY02 | L | 1 | 14 | 10 | 1-8 |  | OK | ↑ | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.10 (01-08)
11 | BJBHT.A23L6 | BLECF_ | 177 | 0x | 00B1 | 6 | Arc | BYPLM.A23L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.09 (09-16)
12 | BJBHT.A22L6 | BLECF_ | 197 | 0x | 00C5 | 6 | Arc | BYPLM.A22L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | G | 6 | 7-8 | BY02 | L | 1 | 13 | 9 | 1-8 |  | OK | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | CFV-SR6-BLML.BLETC.09 (01-08)
13 | BJBHT.A21L6 | BLECF_ | 170 | 0x | 00AA | 6 | Arc | BYPLM.A21L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.08 (09-16)
14 | BJBHT.A20L6 | BLECF_ | 179 | 0x | 00B3 | 6 | Arc | BYPLM.A20L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | G | 4 | 7-8 | BY02 | L | 1 | 11 | 8 | 1-8 | Test in tunnel needed! | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.08 (01-08)
15 | BJBHT.A19L6 | BLECF_ | 178 | 0x | 00B2 | 6 | Arc | BYPLM.A19L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | G | 3 | 7-8 | BY02 | L | 1 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.07 (09-16)
16 | BJBHT.A18L6 | BLECF_ | 207 | 0x | 00CF | 6 | Arc | BYPLM.A18L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | G | 2 | 7-8 | BY02 | L | 1 | 10 | 7 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1410 | [27 empty] | CFV-SR6-BLML.BLETC.07 (01-08) | bar: noise specta 1 to noise specta 4
17 | BJBHT.A17L6 | BLECF_ | 125 | 0x | 007D | 6 | Arc | BYPLM.A17L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | G | 1 | 7-8 | BY02 | L | 1 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1421 | [27 empty] | CFV-SR6-BLML.BLETC.06 (09-16) | bar: noise specta 2 to noise specta 3; noise specta 6
18 | BJBHT.A16L6 | BLECF_ | 708 | 0x | 02C4 | 6 | Arc | BYPLM.A16L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | F | 5 | 7-8 | BY02 | L | 1 | 9 | 6 | 1-8 |  | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.06 (01-08)
19 | BJBHT.A15L6 | BLECF_ | 299 | 0x | 012B | 6 | Arc | BYPLM.A15L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | F | 4 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.05 (09-16) | bar: noise specta 1; noise specta 4 to noise specta 5
20 | BJBHT.A14L6 | BLECF_ | 281 | 0x | 0119 | 6 | Arc | BYPLM.A14L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | F | 3 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 |  | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.05 (01-08) | bar: noise specta 6
21 | BJBHT.A13L6 | BLECF_ | 268 | 0x | 010C | 6 | Arc | BYPLM.A13L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.04 (09-16) | bar: noise specta 6
22 | BJBHT.A12L6 | BLECF_ | 172 | 0x | 00AC | 6 | Arc | BYPLM.A12L6 | 6 | L |  |  |  | 7-8 | SR6 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 7 | 4 | 1-8 | Power loss could be checked | ↑ | OK | OK | ↑ |  |  | OK | OK | OK | OK | ↑ | [36 empty] | CFV-SR6-BLML.BLETC.04 (01-08)
23 | UD62 | BLECF_ | 187 | 0x | 00BB | 8 | UJ63 | BY03 | 6 | CL | 3 | 1 | B | 17-18 | SR6 | BY05 | C | 4 | 5-6 | BY02 | C | 2 | 11 | 8 | 1-8 | Power loss could be checked | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 1994 | up o.k. down not o.k | up o.k. down not o.k | [24 empty] | CFV-SR6-BLMC.BLETC.08 (01-08)
24 | TD62.2 | BLECF_ | 255 | 0x | 00FF | 8 | UJ63 | BY03 | 6 | CL | 2 | 10 | B | 15-16 | SR6 | BY05 | C | 4 | 3-4 | BY02 | C | 2 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.07 (09-16)
25 | TD62.1 | BLECF_ | 511 | 0x | 01FF | 8 | UJ63 | BY03 | 6 | CL | 2 | 9 | B | 13-14 | SR6 | BY05 | C | 4 | 1-2 | BY02 | C | 2 | 10 | 7 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.07 (01-08)
26 | BJBHT.A11L6 | BLECF_ | 108 | 0x | 006C | 6 | UJ63 | BY03 | 6 | CL | 2 | 8 | B | 11-12 | SR6 | BY05 | C | 3 | 11-12 | BY02 | L | 1 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.03 (09-16) | Slava: Expert name missing in MTF | bar: noise specta 4; Modulation 7
27 | BJBHT.A10L6 | BLECF_ | 91 | 0x | 005B | 6 | UJ63 | BY03 | 6 | CL | 2 | 7 | B | 9-10 | SR6 | BY05 | C | 3 | 9-10 | BY02 | L | 1 | 6 | 3 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.03 (01-08) | bar: noise specta 6
28 | BJBHT.A9L6 | BLECF_ | 161 | 0x | 00A1 | 6 | UJ63 | BY03 | 6 | CL | 2 | 6 | B | 7-8 | SR6 | BY05 | C | 3 | 7-8 | BY02 | L | 1 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.02 (09-16)
29 | BJBHT.A8L6 | BLECF_ | 115 | 0x | 0073 | 6 | UJ63 | BY03 | 6 | CL | 2 | 5 | B | 5-6 | SR6 | BY05 | C | 3 | 5-6 | BY02 | L | 1 | 5 | 2 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.02 (01-08)
30 | BJBHT.C5L6 | BLECF_ | 49 | 0x | 0031 | 1 | UJ63 | BY03 | 6 | CL | 2 | 4 | B | 3-4 | SR6 | BY05 | C | 3 | 3-4 | BY02 | C | 2 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1332 | [26 empty] | CFV-SR6-BLMC.BLETC.06 (09-16)
31 | BJBHT.B5L6 | BLECF_ | 429 | 0x | 01AD | 8 | UJ63 | BY03 | 6 | CL | 2 | 3 | B | 1-2 | SR6 | BY05 | C | 3 | 1-2 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.01 (09-16)
32 | BJBHT.A5L6 | BLECF_ | 107 | 0x | 006B | 3 | UJ63 | BY03 | 6 | CL | 2 | 2 | A | 23-24 | SR6 | BY05 | C | 2 | 11-12 | BY02 | C | 2 | 9 | 6 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.06 (01-08) | bar: noise specta 1 to noise specta 3
33 | BJBHT.K4L6 | BLECF_ | 223 | 0x | 00DF | 8 | UJ63 | BY03 | 6 | CL | 2 | 1 | A | 21-22 | SR6 | BY05 | C | 2 | 9-10 | BY02 | L | 1 | 4 | 1 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLML.BLETC.01 (01-08)
34 | BJBHT.J4L6 | BLECF_ | 548 | 0x | 0224 | 5 | UJ63 | BY03 | 6 | CL | 1 | 10 | A | 19-20 | SR6 | BY05 | C | 2 | 7-8 | BY02 | C | 2 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1321 | 1325 | [26 empty] | CFV-SR6-BLMC.BLETC.05 (09-16) | bar: noise specta 1 to noise specta 4
35 | BJBHT.I4L6 | BLECF_ | 508 | 0x | 01FC | 5 | UJ63 | BY03 | 6 | CL | 1 | 9 | A | 17-18 | SR6 | BY05 | C | 2 | 5-6 | BY02 | C | 2 | 8 | 5 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.05 (01-08)
36 | BJBHT.H4L6 | BLECF_ | 336 | 0x | 0150 | 3 | UJ63 | BY03 | 6 | CL | 1 | 8 | A | 15-16 | SR6 | BY05 | C | 2 | 3-4 | BY02 | C | 2 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1317 | 1316 | [26 empty] | CFV-SR6-BLMC.BLETC.04 (09-16)
37 | BJBHT.G4L6 | BLECF_ | 66 | 0x | 0042 | 3 | UJ63 | BY03 | 6 | CL | 1 | 7 | A | 13-14 | SR6 | BY05 | C | 2 | 1-2 | BY02 | C | 2 | 7 | 4 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.04 (01-08)
38 | BJBHT.F4L6 | BLECF_ | 610 | 0x | 0262 | 2 | UJ63 | BY03 | 6 | CL | 1 | 6 | A | 11-12 | SR6 | BY05 | C | 1 | 11-12 | BY02 | C | 2 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1327 | [26 empty] | CFV-SR6-BLMC.BLETC.03 (09-16) | bar: noise specta 1 to noise specta 2
39 | BJBHT.E4L6 | BLECF_ | 392 | 0x | 0188 | 2 | UJ63 | BY03 | 6 | CL | 1 | 5 | A | 9-10 | SR6 | BY05 | C | 1 | 9-10 | BY02 | C | 2 | 6 | 3 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.03 (01-08)
40 | BJBHT.D4L6 | BLECF_ | 612 | 0x | 0264 | 8 | UJ63 | BY03 | 6 | CL | 1 | 4 | A | 7-8 | SR6 | BY05 | C | 1 | 7-8 | BY02 | C | 2 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.02 (09-16) | bar: noise specta 1 to noise specta 8
41 | BJBHT.C4L6 | BLECF_ | 12 | 0x | 000C | 8 | UJ63 | BY03 | 6 | CL | 1 | 3 | A | 5-6 | SR6 | BY05 | C | 1 | 5-6 | BY02 | C | 2 | 5 | 2 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.02 (01-08)
42 | BJBHT.B4L6 | BLECF_ | 436 | 0x | 01B4 | 7 | UJ63 | BY03 | 6 | CL | 1 | 2 | A | 3-4 | SR6 | BY05 | C | 1 | 3-4 | BY02 | C | 2 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.01 (09-16) | bar: noise specta 1 to noise specta 7
43 | BJBHT.A4L6 | BLECF_ | 144 | 0x | 0090 | 7 | UJ63 | BY03 | 6 | CL | 1 | 1 | A | 1-2 | SR6 | BY05 | C | 1 | 1-2 | BY02 | C | 2 | 4 | 1 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.01 (01-08)
44 | BJBHT.A4R6 | BLECF_ | 102 | 0x | 0066 | 7 | UJ67 | BY03 | 6 | CR | 1 | 1 | A | 1-2 | SR6 | BY05 | C | 12 | 1-2 | BY02 | C | 2 | 13 | 9 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.09 (01-08)
45 | BJBHT.B4R6 | BLECF_ | 116 | 0x | 0074 | 7 | UJ67 | BY03 | 6 | CR | 1 | 2 | A | 3-4 | SR6 | BY05 | C | 12 | 3-4 | BY02 | C | 2 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.09 (09-16) | bar: noise specta 1 to noise specta 7
46 | BJBHT.C4R6 | BLECF_ | 156 | 0x | 009C | 8 | UJ67 | BY03 | 6 | CR | 1 | 3 | A | 5-6 | SR6 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.10 (01-08) | bar: noise specta 2 to noise specta 8
47 | BJBHT.D4R6 | BLECF_ | 202 | 0x | 00CA | 8 | UJ67 | BY03 | 6 | CR | 1 | 4 | A | 7-8 | SR6 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.10 (09-16) | bar: noise specta 1 to noise specta 8
48 | BJBHT.E4R6 | BLECF_ | 167 | 0x | 00A7 | 2 | UJ67 | BY03 | 6 | CR | 1 | 5 | A | 9-10 | SR6 | BY05 | C | 12 | 9-10 | BY02 | C | 2 | 15 | 11 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.11 (01-08)
49 | BJBHT.F4R6 | BLECF_ | 545 | 0x | 0221 | 2 | UJ67 | BY03 | 6 | CR | 1 | 6 | A | 11-12 | SR6 | BY05 | C | 12 | 11-12 | BY02 | C | 2 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.11 (09-16) | bar: noise specta 1 to noise specta 2
50 | BJBHT.G4R6 | BLECF_ | 219 | 0x | 00DB | 3 | UJ67 | BY03 | 6 | CR | 1 | 7 | A | 13-14 | SR6 | BY05 | C | 11 | 1-2 | BY02 | C | 2 | 16 | 12 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.12 (01-08)
51 | BJBHT.H4R6 | BLECF_ | 45 | 0x | 002D | 3 | UJ67 | BY03 | 6 | CR | 1 | 8 | A | 15-16 | SR6 | BY05 | C | 11 | 3-4 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.12 (09-16) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1
52 | BJBHT.I4R6 | BLECF_ | 173 | 0x | 00AD | 5 | UJ67 | BY03 | 6 | CR | 1 | 9 | A | 17-18 | SR6 | BY05 | C | 11 | 5-6 | BY02 | C | 2 | 17 | 13 | 1-8 |  | OK | ↑ | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.13 (01-08)
53 | BJBHT.J4R6 | BLECF_ | 262 | 0x | 0106 | 4 | UJ67 | BY03 | 6 | CR | 1 | 10 | A | 19-20 | SR6 | BY05 | C | 11 | 7-8 | BY02 | C | 2 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.13 (09-16) | bar: noise specta 1 to noise specta 4
54 | BJBHT.K4R6 | BLECF_ | 198 | 0x | 00C6 | 8 | UJ67 | BY03 | 6 | CR | 2 | 1 | A | 21-22 | SR6 | BY05 | C | 11 | 9-10 | BY02 | R | 3 | 4 | 1 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1331 | [26 empty] | CFV-SR6-BLMR.BLETC.01 (01-08)
55 | BJBHT.A5R6 | BLECF_ | 289 | 0x | 0121 | 3 | UJ67 | BY03 | 6 | CR | 2 | 2 | A | 23-24 | SR6 | BY05 | C | 11 | 11-12 | BY02 | C | 2 | 18 | 14 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1413 | [27 empty] | CFV-SR6-BLMC.BLETC.14 (01-08) | bar: noise specta 1 to noise specta 3
56 | BJBHT.B5R6 | BLECF_ | 165 | 0x | 00A5 | 8 | UJ67 | BY03 | 6 | CR | 2 | 3 | B | 1-2 | SR6 | BY05 | C | 10 | 1-2 | BY02 | R | 3 | 4 | 1 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.01 (09-16)
57 | BJBHT.C5R6 | BLECF_ | 88 | 0x | 0058 | 1 | UJ67 | BY03 | 6 | CR | 2 | 4 | B | 3-4 | SR6 | BY05 | C | 10 | 3-4 | BY02 | C | 2 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.14 (09-16)
58 | BJBHT.A8R6 | BLECF_ | 159 | 0x | 009F | 6 | UJ67 | BY03 | 6 | CR | 2 | 5 | B | 5-6 | SR6 | BY05 | C | 10 | 5-6 | BY02 | R | 3 | 5 | 2 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.02 (01-08)
59 | BJBHT.A9R6 | BLECF_ | 542 | 0x | 021E | 6 | UJ67 | BY03 | 6 | CR | 2 | 6 | B | 7-8 | SR6 | BY05 | C | 10 | 7-8 | BY02 | R | 3 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1330 | [26 empty] | CFV-SR6-BLMR.BLETC.02 (09-16)
60 | BJBHT.A10R6 | BLECF_ | 164 | 0x | 00A4 | 6 | UJ67 | BY03 | 6 | CR | 2 | 7 | B | 9-10 | SR6 | BY05 | C | 10 | 9-10 | BY02 | R | 3 | 6 | 3 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.03 (01-08)
61 | BJBHT.A11R6 | BLECF_ | 72 | 0x | 0048 | 6 | UJ67 | BY03 | 6 | CR | 2 | 8 | B | 11-12 | SR6 | BY05 | C | 10 | 11-12 | BY02 | R | 3 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1321 | 1324 | [26 empty] | CFV-SR6-BLMR.BLETC.03 (09-16) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1 to Modulation 8
62 | TD68.1 | BLECF_ | 391 | 0x | 0187 | 8 | UJ67 | BY03 | 6 | CR | 2 | 9 | B | 13-14 | SR6 | BY05 | C | 9 | 1-2 | BY02 | C | 2 | 19 | 15 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1406 | [27 empty] | CFV-SR6-BLMC.BLETC.15 (01-08) | Slava: Expert name missing in MTF | bar: Modulation 6
63 | TD68.2 | BLECF_ | 56 | 0x | 0038 | 8 | UJ67 | BY03 | 6 | CR | 2 | 10 | B | 15-16 | SR6 | BY05 | C | 9 | 3-4 | BY02 | C | 2 | 19 | 15 | 9-16 |  | OK | ↑ | OK | OK |  |  | OK | OK | ↑ | OK | ↑ | [36 empty] | CFV-SR6-BLMC.BLETC.15 (09-16)
64 | UD68 | BLECF_ | 82 | 0x | 0052 | 8 | UJ67 | BY03 | 6 | CR | 3 | 1 | B | 17-18 | SR6 | BY05 | C | 9 | 5-6 | BY02 | C | 2 | 20 | 16 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMC.BLETC.16 (01-08)
65 | BJBHT.A12R6 | BLECF_ | 527 | 0x | 020F | 6 | Arc | BYPLM.A12R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | F | 8 | 7-8 | BY02 | R | 3 | 7 | 4 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.04 (01-08)
66 | BJBHT.A13R6 | BLECF_ | 230 | 0x | 00E6 | 6 | Arc | BYPLM.A13R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1412 | [27 empty] | CFV-SR6-BLMR.BLETC.04 (09-16)
67 | BJBHT.A14R6 | BLECF_ | 532 | 0x | 0214 | 6 | Arc | BYPLM.A14R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | F | 10 | 7-8 | BY02 | R | 3 | 8 | 5 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.05 (01-08)
68 | BJBHT.A15R6 | BLECF_ | 569 | 0x | 0239 | 6 | Arc | BYPLM.A15R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | F | 11 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.05 (09-16)
69 | BJBHT.A16R6 | BLECF_ | 274 | 0x | 0112 | 6 | Arc | BYPLM.A16R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | F | 12 | 7-8 | BY02 | R | 3 | 9 | 6 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.06 (01-08)
70 | BJBHT.A17R6 | BLECF_ | 301 | 0x | 012D | 6 | Arc | BYPLM.A17R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | G | 7 | 7-8 | BY02 | R | 3 | 9 | 6 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.06 (09-16)
71 | BJBHT.A18R6 | BLECF_ | 19 | 0x | 0013 | 6 | Arc | BYPLM.A18R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | G | 8 | 7-8 | BY02 | R | 3 | 10 | 7 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.07 (01-08) | bar: noise specta 1 to noise specta 6
72 | BJBHT.A19R6 | BLECF_ | 563 | 0x | 0233 | 6 | Arc | BYPLM.A19R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | G | 9 | 7-8 | BY02 | R | 3 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.07 (09-16)
73 | BJBHT.A20R6 | BLECF_ | 566 | 0x | 0236 | 6 | Arc | BYPLM.A20R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 11 | 8 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.08 (01-08)
74 | BJBHT.A21R6 | BLECF_ | 295 | 0x | 0127 | 6 | Arc | BYPLM.A21R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 11 | 8 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.08 (09-16)
75 | BJBHT.A22R6 | BLECF_ | 28 | 0x | 001C | 6 | Arc | BYPLM.A22R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | G | 12 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 | Test in tunnel needed! | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.09 (01-08) | bar: noise specta 1 to noise specta 6
76 | BJBHT.A23R6 | BLECF_ | 540 | 0x | 021C | 6 | Arc | BYPLM.A23R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | H | 7 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.09 (09-16)
77 | BJBHT.A24R6 | BLECF_ | 364 | 0x | 016C | 6 | Arc | BYPLM.A24R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 14 | 10 | 1-8 |  | OK | OK | OK | ↑ |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.10 (01-08)
78 | BJBHT.A25R6 | BLECF_ | 555 | 0x | 022B | 6 | Arc | BYPLM.A25R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | H | 9 | 7-8 | BY02 | R | 3 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1410 | [27 empty] | CFV-SR6-BLMR.BLETC.10 (09-16)
79 | BJBHT.A26R6 | BLECF_ | 564 | 0x | 0234 | 6 | Arc | BYPLM.A26R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | H | 10 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 | Test in tunnel needed! | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.11 (01-08)
80 | BJBHT.A27R6 | BLECF_ | 557 | 0x | 022D | 6 | Arc | BYPLM.A27R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1328 | [26 empty] | CFV-SR6-BLMR.BLETC.11 (09-16)
81 | BJBHT.A28R6 | BLECF_ | 63 | 0x | 003F | 6 | Arc | BYPLM.A28R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | H | 12 | 7-8 | BY02 | R | 3 | 16 | 12 | 1-8 |  | ↑ | ↑ | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.12 (01-08) | bar: noise specta 2 to noise specta 6
82 | BJBHT.A29R6 | BLECF_ | 561 | 0x | 0231 | 6 | Arc | BYPLM.A29R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.12 (09-16)
83 | BJBHT.A30R6 | BLECF_ | 565 | 0x | 0235 | 6 | Arc | BYPLM.A30R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | I | 8 | 7-8 | BY02 | R | 3 | 17 | 13 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.13 (01-08)
84 | BJBHT.A31R6 | BLECF_ | 210 | 0x | 00D2 | 6 | Arc | BYPLM.A31R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | I | 9 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.13 (09-16)
85 | BJBHT.A32R6 | BLECF_ | 180 | 0x | 00B4 | 6 | Arc | BYPLM.A32R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | I | 10 | 7-8 | BY02 | R | 3 | 18 | 14 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [10 empty] | up not o.k down o.k | [25 empty] | CFV-SR6-BLMR.BLETC.14 (01-08)
86 | BJBHT.A33R6 | BLECF_ | 538 | 0x | 021A | 6 | Arc | BYPLM.A33R6 | 6 | R |  |  |  | 7-8 | SR6 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 18 | 14 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.14 (09-16)
87 | BJBHT.A34R6 | BLECF_ | 176 | 0x | 00B0 | 6 | Arc | BYPLM.A34R6 | 6 | R |  |  |  | 7-9 | SR6 | BY05 | I | 12 | 7-8 | BY02 | R | 3 | 19 | 15 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | CFV-SR6-BLMR.BLETC.15 (01-08)
last entry 23/6/08
| Door | [7 empty] | Transformer soldered
[50 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA
[6 empty] | Card number correct | [43 empty] | noise specta 4: < 100 BLMbits; Modulation 4: o.k.; 10pA 4: o.k.
|  |  |  | 0x | 0000 | Card number needs to be checked
|  |  |  | 0x | 0000 | Card number unknown need to be checked in the tunnel | [43 empty] | noise specta 4: 100-300 BLMbits; Modulation 4: Prob. values mod; 10pA 4: to small values 20s
|  | BLECF_ | 656 | Card was exchanged, Data base need to be checked for the correct number | [45 empty] | noise specta 4: > 300 BLMbits; Modulation 4: Prob. Data base; 10pA 4: Prob. to be checked
[53 empty] | > 522 BLMbits | [7 empty] | Flag missing in DB
[51 empty] | n |  | no data
Note on AW3: effinger: 3 cases needed to be verified by with expert application
Note on AA18: effinger: A20L6; Jumper was not conneted properly; Card working corectly: reception o.k.
Note on AH28: effinger LF A&B 8.9.09 ! O.k 23.9.09
Note on AR30: effinger: Level was blimking (23.9)
Note on AS30: effinger: Level was blimking (23.9)
Note on AT30: effinger: CFC-ERROR Level was blimking (23.9)
Note on BM31: jemery: Missing expert name
Note on AJ38: effinger: increasing while check on 23.9
Note on BG57: jemery: Low amplitude
Note on AI58: effinger: LF while check 29.9.09
Note on AJ58: effinger: EERC while check 29.9.09
Note on AL58: effinger: FID while check 29.9.09
Note on BK67: jemery: Amplitude low phase higher
Note on BL68: jemery: Missing monitor
Note on AT69: effinger: CFC-ERROR
Note on AJ72: effinger: increasing while last check 23.09.09
Note on AA82: effinger: CFC Card not working correctly-> reset -> o.k
Note on AA86: effinger: CFC Card not working correctly-> reset -> o.k
Note on AJ92: effinger: increasing while last check 23.09.09
Note on D104: effinger: 565 original number chnaged to 656
Note on BH106: jemery: Spare for phase 2

## Point 7
SR7 | Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA | [7 empty] | Expert Name |  | HV Levels | HV Levels | HV Levels | HV Levels
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | other | Scan 23.7.09 | Scan | Scan | Scan
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 09.09.09 |  | 07.10.09 |  | 13.10.09 |  | 13.10.09 |  |  |  |  | noise specta 1: 10.10 and 12.10; Modulation 1: 8.10 and 12.10 |  | Comments |  | 14.09.09 | 02.10.09 | 12.10.09
1 | BJBHT.A33L7 | BLECF_ | 69 | 0x | 0045 | 6 | Arc | BYPLM.A33L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | I | 5 | 7-8 | BY02 | L | 1 | 19 | 15 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR7-BLML.BLETC.15 (09-16)
2 | BJBHT.A32L7 | BLECF_ | 122 | 0x | 007A | 6 | Arc | BYPLM.A32L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | I | 4 | 7-8 | BY02 | L | 1 | 19 | 15 | 1-8 |  | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLML.BLETC.15 (01-08)
3 | BJBHT.A31L7 | BLECF_ | 426 | 0x | 01AA | 6 | Arc | BYPLM.A31L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | I | 3 | 7-8 | BY02 | L | 1 | 18 | 14 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 3000 BLMbits | CFV-SR7-BLML.BLETC.14 (09-16) |  |  | 1326
4 | BJBHT.A30L7 | BLECF_ | 508 | 0x | 01FC | 6 | Arc | BYPLM.A30L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | I | 2 | 7-8 | BY02 | L | 1 | 18 | 14 | 1-8 | to be check in tunnel with TB | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLML.BLETC.14 (01-08)
5 | BJBHT.A29L7 | BLECF_ | 123 | 0x | 007B | 6 | Arc | BYPLM.A29L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | I | 1 | 7-8 | BY02 | L | 1 | 17 | 13 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLML.BLETC.13 (09-16)
6 | BJBHT.A28L7 | BLECF_ | 20 | 0x | 0014 | 6 | Arc | BYPLM.A28L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | H | 6 | 7-8 | BY02 | L | 1 | 17 | 13 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLML.BLETC.13 (01-08)
7 | BJBHT.A27L7 | BLECF_ | 140 | 0x | 008C | 6 | Arc | BYPLM.A27L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | H | 5 | 7-8 | BY02 | L | 1 | 16 | 12 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR7-BLML.BLETC.12 (09-16)
8 | BJBHT.A26L7 | BLECF_ | 126 | 0x | 007E | 6 | Arc | BYPLM.A26L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 16 | 12 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR7-BLML.BLETC.12 (01-08)
9 | BJBHT.A25L7 | BLECF_ | 43 | 0x | 002B | 6 | Arc | BYPLM.A25L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | H | 3 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 200 BLMbits | CFV-SR7-BLML.BLETC.11 (09-16)
10 | BJBHT.A24L7 | BLECF_ | 454 | 0x | 01C6 | 6 | Arc | BYPLM.A24L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | H | 2 | 7-8 | BY02 | L | 1 | 15 | 11 | 1-8 |  | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.11 (01-08)
11 | BJBHT.A23L7 | BLECF_ | 17 | 0x | 0011 | 6 | Arc | BYPLM.A23L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 400 BLMbits | CFV-SR7-BLML.BLETC.10 (09-16)
12 | BJBHT.A22L7 | BLECF_ | 47 | 0x | 002F | 6 | Arc | BYPLM.A22L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | G | 6 | 7-8 | BY02 | L | 1 | 14 | 10 | 1-8 |  | OK | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 400 BLMbits | CFV-SR7-BLML.BLETC.10 (01-08)
13 | BJBHT.A21L7 | BLECF_ | 87 | 0x | 0057 | 6 | Arc | BYPLM.A21L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 |  | OK | ↑ | OK | ↑ | OK | ↑ | OK | OK | ↑ | OK | ↑ | 10pA 4: 600 BLMbits | CFV-SR7-BLML.BLETC.09 (09-16) |  | 1403
14 | BJBHT.A20L7 | BLECF_ | 74 | 0x | 004A | 6 | Arc | BYPLM.A20L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | G | 4 | 7-8 | BY02 | L | 1 | 13 | 9 | 1-8 |  | ↑ | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLML.BLETC.09 (01-08)
15 | BJBHT.A19L7 | BLECF_ | 466 | 0x | 01D2 | 6 | Arc | BYPLM.A19L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | G | 3 | 7-8 | BY02 | L | 1 | 11 | 8 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.08 (09-16) | bar: 10pA 1
16 | BJBHT.A18L7 | BLECF_ | 571 | 0x | 023B | 6 | Arc | BYPLM.A18L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | G | 2 | 7-8 | BY02 | L | 1 | 11 | 8 | 1-8 | to be check in tunnel with TB | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.08 (01-08) |  | 1402
17 | BJBHT.A17L7 | BLECF_ | 430 | 0x | 01AE | 6 | Arc | BYPLM.A17L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | G | 1 | 7-8 | BY02 | L | 1 | 10 | 7 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.07 (09-16)
18 | BJBHT.A16L7 | BLECF_ | 39 | 0x | 0027 | 6 | Arc | BYPLM.A16L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | F | 5 | 7-8 | BY02 | L | 1 | 10 | 7 | 1-8 |  | OK | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 300 BLMbits | CFV-SR7-BLML.BLETC.07 (01-08)
19 | BJBHT.A15L7 | BLECF_ | 534 | 0x | 0216 | 6 | Arc | BYPLM.A15L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | F | 4 | 7-8 | BY02 | L | 1 | 9 | 6 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.06 (09-16) | bar: noise specta 2 to noise specta 3; noise specta 6; 10pA 6
20 | BJBHT.A14L7 | BLECF_ | 461 | 0x | 01CD | 6 | Arc | BYPLM.A14L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | F | 3 | 7-8 | BY02 | L | 1 | 9 | 6 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR7-BLML.BLETC.06 (01-08) |  | 0
21 | BJBHT.A13L7 | BLECF_ | 449 | 0x | 01C1 | 6 | Arc | BYPLM.A13L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.05 (09-16)
22 | BJBHT.A12L7 | BLECF_ | 68 | 0x | 0044 | 6 | Arc | BYPLM.A12L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLML.BLETC.05 (01-08)
23 | BJBHT.B11L7 | BLECF_ | 469 | 0x | 01D5 | 8 | RR73 | BY01 | 7 | CL | 3 | 8 | F | 1-2 | SR7 | BY05 | C | 5 | 1-2 | BY02 | L | 1 | 7 | 4 | 9-16 | was wrong conneted on patch | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLML.BLETC.04 (09-16) |  |  |  | 1315
24 | BJBHT.A11L7 | BLECF_ | 679 | 0x | 02A7 | 8 | RR73 | BY01 | 7 | CL | 3 | 7 | E | 5-6 | SR7 | BY05 | C | 5 | 5-6 | BY02 | C | 4 | 5 | 2 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.02 (09-16) |  | 0
25 | BJBHT.A10L7 | BLECF_ | 544 | 0x | 0220 | 8 | RR73 | BY01 | 7 | CL | 3 | 6 | E | 3-4 | SR7 | BY05 | C | 5 | 3-4 | BY02 | L | 1 | 7 | 4 | 1-8 |  | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLML.BLETC.04 (01-08) | Ewald & Ion: Card exchange due to noise problems
26 | BJBHT.B9L7 | BLECF_ | 678 | 0x | 02A6 | 8 | RR73 | BY01 | 7 | CL | 3 | 5 | E | 1-2 | SR7 | BY05 | C | 5 | 1-2 | BY02 | L | 1 | 6 | 3 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.03 (09-16) | bar: 10pA 2 to 10pA 8
27 | BJBHT.A9L7 | BLECF_ | 559 | 0x | 022F | 8 | RR73 | BY01 | 7 | CL | 3 | 4 | D | 23-24 | SR7 | BY05 | C | 4 | 11-12 | BY02 | E | 4 | 5 | 2 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLME.BLETC.02 (01-08) |  | 0 | 1323
28 | BJBHT.B8L7 | BLECF_ | 649 | 0x | 0289 | 6 | RR73 | BY01 | 7 | CL | 3 | 3 | D | 21-22 | SR7 | BY05 | C | 4 | 9-10 | BY02 | L | 1 | 6 | 3 | 1-8 |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLML.BLETC.03 (01-08)
29 | BJBHT.A8L7 | BLECF_ | 462 | 0x | 01CE | 3 | RR73 | BY01 | 7 | CL | 3 | 2 | D | 19-20 | SR7 | BY05 | C | 4 | 7-8 | BY02 | E | 4 | 4 | 1 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLME.BLETC.01 (09-16) |  | 0 | 1202
30 | BJBHT.B7L7 | BLECF_ | 513 | 0x | 0201 | 7 | RR73 | BY01 | 7 | CL | 3 | 1 | D | 17-18 | SR7 | BY05 | C | 4 | 5-6 | BY02 | L | 1 | 5 | 2 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.02 (09-16)
31 | BJBHT.A7L7 | BLECF_ | 411 | 0x | 019B | 2 | RR73 | BY01 | 7 | CL | 2 | 10 | D | 15-16 | SR7 | BY05 | C | 4 | 3-4 | BY02 | E | 4 | 4 | 1 | 1-8 |  | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLME.BLETC.01 (01-08) | Jonathan and Ion: check in the tunnel necessary | 0 | 1276
32 | BJBHT.I6L7 | BLECF_ | 587 | 0x | 024B | 7 | RR73 | BY01 | 7 | CL | 2 | 9 | D | 13-14 | SR7 | BY05 | C | 4 | 1-2 | BY02 | L | 1 | 5 | 2 | 1-8 |  | ↑ | OK | OK | ↑ | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLML.BLETC.02 (01-08) | bar: noise specta 5 to noise specta 7
33 | BJBHT.H6L7 | BLECF_ | 118 | 0x | 0076 | 4 | RR73 | BY01 | 7 | CL | 2 | 8 | D | 11-12 | SR7 | BY05 | C | 3 | 11-12 | BY02 | C | 2 | 11 | 8 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.08 (09-16) | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1
34 | BJBHT.G6L7 | BLECF_ | 191 | 0x | 00BF | 4 | RR73 | BY01 | 7 | CL | 2 | 7 | D | 9-10 | SR7 | BY05 | C | 3 | 9-10 | BY02 | C | 2 | 11 | 8 | 1-8 |  | ↑ | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.08 (01-08) |  |  | 1322
35 | BJBHT.F6L7 | BLECF_ | 434 | 0x | 01B2 | 7 | RR73 | BY01 | 7 | CL | 2 | 6 | D | 7-8 | SR7 | BY05 | C | 3 | 7-8 | BY02 | C | 2 | 10 | 7 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.07 (09-16) | bar: noise specta 1 to noise specta 7
36 | BJBHT.E6L7 | BLECF_ | 560 | 0x | 0230 | 7 | RR73 | BY01 | 7 | CL | 2 | 5 | D | 5-6 | SR7 | BY05 | C | 3 | 5-6 | BY02 | C | 2 | 10 | 7 | 1-8 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.07 (01-08) |  | 0 | 0 | 1335
37 | BJBHT.D6L7 | BLECF_ | 355 | 0x | 0163 | 3 | RR73 | BY01 | 7 | CL | 2 | 4 | D | 3-4 | SR7 | BY05 | C | 3 | 3-4 | BY02 | C | 2 | 9 | 6 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.06 (09-16)
38 | BJBHT.C6L7 | BLECF_ | 553 | 0x | 0229 | 3 | RR73 | BY01 | 7 | CL | 2 | 3 | D | 1-2 | SR7 | BY05 | C | 3 | 1-2 | BY02 | C | 2 | 9 | 6 | 1-8 |  | OK | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | noise specta 1: n; noise specta 2: n; noise specta 3: n; 10pA 4: 1200 BLMbits | CFV-SR7-BLMC.BLETC.06 (01-08)
39 | BJBHT.B6L7 | BLECF_ | 682 | 0x | 02AA | 7 | RR73 | BY01 | 7 | CL | 2 | 2 | C | 23-24 | SR7 | BY05 | C | 2 | 11-12 | BY02 | C | 2 | 8 | 5 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.05 (09-16) | Slava: Spare channels: Phase 2 | bar: noise specta 1 to noise specta 7; Modulation 1
40 | BJBHT.A6L7 | BLECF_ | 465 | 0x | 01D1 | 7 | RR73 | BY01 | 7 | CL | 2 | 1 | C | 21-22 | SR7 | BY05 | C | 2 | 9-10 | BY02 | C | 2 | 8 | 5 | 1-8 |  | ↑ | OK | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | 10pA 4: 1500 BLMbits | CFV-SR7-BLMC.BLETC.05 (01-08) | Slava: Spare channels: Phase 2 |  |  | 1331
41 | BJBHT.E5L7 | BLECF_ | 96 | 0x | 0060 | 6 | RR73 | BY01 | 7 | CL | 1 | 10 | C | 19-20 | SR7 | BY05 | C | 2 | 7-8 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLML.BLETC.01 (09-16) |  |  |  | ON 2 o.k. / Off o.k
42 | BJBHT.D5L7 | BLECF_ | 94 | 0x | 005E | 6 | RR73 | BY01 | 7 | CL | 1 | 9 | C | 17-18 | SR7 | BY05 | C | 2 | 5-6 | BY02 | C | 2 | 7 | 4 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.04 (09-16) | Slava: Spare channels: Phase 2 | 0 | bar: noise specta 1 to noise specta 6; Modulation 6
43 | BJBHT.C5L7 | BLECF_ | 273 | 0x | 0111 | 6 | RR73 | BY01 | 7 | CL | 1 | 8 | C | 15-16 | SR7 | BY05 | C | 2 | 3-4 | BY02 | C | 2 | 7 | 4 | 1-8 |  | OK | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 1400 BLMbits | CFV-SR7-BLMC.BLETC.04 (01-08) | Slava: Spare channels: Phase 2
44 | BJBHT.B5L7 | BLECF_ | 590 | 0x | 024E | 8 | RR73 | BY01 | 7 | CL | 1 | 7 | C | 13-14 | SR7 | BY05 | C | 2 | 1-2 | BY02 | C | 2 | 6 | 3 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.03 (09-16) | Slava: Spare channels: Phase 2 | 0 | bar: noise specta 1 to noise specta 8; Modulation 8
45 | BJBHT.A5L7 | BLECF_ | 1 | 0x | 0001 | 8 | RR73 | BY01 | 7 | CL | 1 | 6 | C | 11-12 | SR7 | BY05 | C | 1 | 11-12 | BY02 | C | 2 | 6 | 3 | 1-8 |  | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1500 BLMbits | CFV-SR7-BLMC.BLETC.03 (01-08) | Slava: Spare channels: Phase 2
46 | BJBHT.E4L6 | BLECF_ | 372 | 0x | 0174 | 6 | RR73 | BY01 | 7 | CL | 1 | 5 | C | 9-10 | SR7 | BY05 | C | 1 | 9-10 | BY02 | L | 1 | 4 | 1 | 1-8 |  | ↑ | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLML.BLETC.01 (01-08) |  |  |  | ON o.k / Off KO
47 | BJBHT.D4L6 | BLECF_ | 445 | 0x | 01BD | 6 | RR73 | BY01 | 7 | CL | 1 | 4 | C | 7-8 | SR7 | BY05 | C | 1 | 7-8 | BY02 | C | 2 | 5 | 2 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.02 (09-16) | Slava: Spare channels: Phase 2 | 0 | bar: noise specta 1 to noise specta 6; Modulation 3 to Modulation 6
48 | BJBHT.C4L6 | BLECF_ | 369 | 0x | 0171 | 6 | RR73 | BY01 | 7 | CL | 1 | 3 | C | 5-6 | SR7 | BY05 | C | 1 | 5-6 | BY02 | C | 2 | 5 | 2 | 1-8 |  | ↑ | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLMC.BLETC.02 (01-08) | Slava: Spare channels: Phase 2 |  | 1302
49 | BJBHT.B4L6 | BLECF_ | 633 | 0x | 0279 | 6 | RR73 | BY01 | 7 | CL | 1 | 2 | C | 3-4 | SR7 | BY05 | C | 1 | 3-4 | BY02 | C | 2 | 4 | 1 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.01 (09-16) |  | 0 | bar: noise specta 1 to noise specta 6
50 | BJBHT.A4L6 | BLECF_ | 308 | 0x | 0134 | 6 | RR73 | BY01 | 7 | CL | 1 | 1 | C | 1-2 | SR7 | BY05 | C | 1 | 1-2 | BY02 | C | 2 | 4 | 1 | 1-8 |  | OK | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLMC.BLETC.01 (01-08)
51 | BJBHT.A4R7 | BLECF_ | 443 | 0x | 01BB | 6 | RR77 | BY02 | 7 | CR | 1 | 1 | C | 1-2 | SR7 | BY05 | C | 12 | 1-2 | BY02 | C | 2 | 13 | 9 | 1-8 |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLMC.BLETC.09 (01-08)
52 | BJBHT.B4R7 | BLECF_ | 455 | 0x | 01C7 | 6 | RR77 | BY02 | 7 | CR | 1 | 2 | C | 3-4 | SR7 | BY05 | C | 12 | 3-4 | BY02 | C | 2 | 13 | 9 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.09 (09-16) | bar: noise specta 1 to noise specta 6
53 | BJBHT.C4R7 | BLECF_ | 351 | 0x | 015F | 6 | RR77 | BY02 | 7 | CR | 1 | 3 | C | 5-6 | SR7 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.10 (01-08) | Slava: Spare channels: Phase 2 | bar: Modulation 1 to Modulation 4
54 | BJBHT.D4R7 | BLECF_ | 431 | 0x | 01AF | 6 | RR77 | BY02 | 7 | CR | 1 | 4 | C | 7-8 | SR7 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.10 (09-16) | Slava: Spare channels: Phase 2 | bar: noise specta 1 to noise specta 6; Modulation 1 to Modulation 4
55 | BJBHT.E4R7 | BLECF_ | 420 | 0x | 01A4 | 6 | RR77 | BY02 | 7 | CR | 1 | 5 | C | 9-10 | SR7 | BY05 | C | 12 | 9-10 | BY02 | R | 3 | 4 | 1 | 1-8 |  |  |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1400 BLMbits | CFV-SR7-BLMR.BLETC.01 (01-08) |  | 1284
56 | BJBHT.A5R7 | BLECF_ | 412 | 0x | 019C | 8 | RR77 | BY02 | 7 | CR | 1 | 6 | C | 11-12 | SR7 | BY05 | C | 12 | 11-12 | BY02 | C | 2 | 15 | 11 | 1-8 |  | OK | ↑ | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 1: 6000; 10pA 4: 1200 BLMbits | CFV-SR7-BLMC.BLETC.11 (01-08) | Slava: Spare channels: Phase 2
57 | BJBHT.B5R7 | BLECF_ | 446 | 0x | 01BE | 8 | RR77 | BY02 | 7 | CR | 1 | 7 | C | 13-14 | SR7 | BY05 | C | 11 | 1-2 | BY02 | C | 2 | 15 | 11 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.11 (09-16) | Slava: Spare channels: Phase 2 | bar: noise specta 1 to noise specta 7; Modulation 1
58 | BJBHT.C5R7 | BLECF_ | 421 | 0x | 01A5 | 6 | RR77 | BY02 | 7 | CR | 1 | 8 | C | 15-16 | SR7 | BY05 | C | 11 | 3-4 | BY02 | C | 2 | 16 | 12 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR7-BLMC.BLETC.12 (01-08)
59 | BJBHT.D5R7 | BLECF_ | 415 | 0x | 019F | 6 | RR77 | BY02 | 7 | CR | 1 | 9 | C | 17-18 | SR7 | BY05 | C | 11 | 5-6 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.12 (09-16) | bar: noise specta 1 to noise specta 7
60 | BJBHT.E5R7 | BLECF_ | 368 | 0x | 0170 | 6 | RR77 | BY02 | 7 | CR | 1 | 10 | C | 19-20 | SR7 | BY05 | C | 11 | 7-8 | BY02 | R | 3 | 4 | 1 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.01 (09-16) |  | 0 |  |  | 1332 | bar: 10pA 2
61 | BJBHT.A6R7 | BLECF_ | 334 | 0x | 014E | 4 | RR77 | BY02 | 7 | CR | 2 | 1 | C | 21-22 | SR7 | BY05 | C | 11 | 9-10 | BY02 | C | 2 | 17 | 13 | 1-8 |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.13 (01-08) | bar: noise specta 1
62 | BJBHT.B6R7 | BLECF_ | 31 | 0x | 001F | 4 | RR77 | BY02 | 7 | CR | 2 | 2 | C | 23-24 | SR7 | BY05 | C | 11 | 11-12 | BY02 | C | 2 | 17 | 13 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.13 (09-16)
63 | BJBHT.C6R7 | BLECF_ | 350 | 0x | 015E | 5 | RR77 | BY02 | 7 | CR | 2 | 3 | D | 1-2 | SR7 | BY05 | C | 10 | 1-2 | BY02 | C | 2 | 18 | 14 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1400 BLMbits | CFV-SR7-BLMC.BLETC.14 (01-08) | Slava: Spare channels: Phase 2
64 | BJBHT.D6R7 | BLECF_ | 81 | 0x | 0051 | 5 | RR77 | BY02 | 7 | CR | 2 | 4 | D | 3-4 | SR7 | BY05 | C | 10 | 3-4 | BY02 | C | 2 | 18 | 14 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.14 (09-16) | Slava: Spare channels: Phase 2 | bar: noise specta 1 to noise specta 6; Modulation 3
65 | BJBHT.E6R7 | BLECF_ | 394 | 0x | 018A | 8 | RR77 | BY02 | 7 | CR | 2 | 5 | D | 5-6 | SR7 | BY05 | C | 10 | 5-6 | BY02 | C | 2 | 19 | 15 | 1-8 |  | ↑ | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.15 (01-08)
66 | BJBHT.F6R7 | BLECF_ | 13 | 0x | 000D | 8 | RR77 | BY02 | 7 | CR | 2 | 6 | D | 7-8 | SR7 | BY05 | C | 10 | 7-8 | BY02 | C | 2 | 19 | 15 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.15 (09-16) | bar: noise specta 1 to noise specta 8
67 | BJBHT.G6R7 | BLECF_ | 433 | 0x | 01B1 | 4 | RR77 | BY02 | 7 | CR | 2 | 7 | D | 9-10 | SR7 | BY05 | C | 10 | 9-10 | BY02 | C | 2 | 20 | 16 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.16 (01-08) | bar: noise specta 1 to noise specta 4; 10pA 2 to 10pA 4
68 | BJBHT.H6R7 | BLECF_ | 482 | 0x | 01E2 | 4 | RR77 | BY02 | 7 | CR | 2 | 8 | D | 11-12 | SR7 | BY05 | C | 10 | 11-12 | BY02 | C | 2 | 20 | 16 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMC.BLETC.16 (09-16) | bar: 10pA 2; 10pA 8
69 | BJBHT.I6R7 | BLECF_ | 464 | 0x | 01D0 | 7 | RR77 | BY02 | 7 | CR | 2 | 9 | D | 13-14 | SR7 | BY05 | C | 9 | 1-2 | BY02 | R | 3 | 5 | 2 | 1-8 |  |  |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.02 (01-08)
70 | BJBHT.A7R7 | BLECF_ | 359 | 0x | 0167 | 2 | RR77 | BY02 | 7 | CR | 2 | 10 | D | 15-16 | SR7 | BY05 | C | 9 | 3-4 | BY02 | E | 4 | 13 | 9 | 1-8 |  | ↑ | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLME.BLETC.09 (01-08) |  | 0 | 1304
71 | BJBHT.B7R7 | BLECF_ | 470 | 0x | 01D6 | 7 | RR77 | BY02 | 7 | CR | 3 | 1 | D | 17-18 | SR7 | BY05 | C | 9 | 5-6 | BY02 | R | 3 | 5 | 2 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.02 (09-16)
72 | BJBHT.A8R7 | BLECF_ | 700 | 0x | 02BC | 3 | RR77 | BY02 | 7 | CR | 3 | 2 | D | 19-20 | SR7 | BY05 | C | 9 | 7-8 | BY02 | E | 4 | 13 | 9 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLME.BLETC.09 (09-16) |  | 0 | 1300 | bar: noise specta 1; noise specta 3
73 | BJBHT.B8R7 | BLECF_ | 358 | 0x | 0166 | 6 | RR77 | BY02 | 7 | CR | 3 | 3 | D | 21-22 | SR7 | BY05 | C | 9 | 9-10 | BY02 | R | 3 | 6 | 3 | 1-8 |  |  |  | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.03 (01-08)
74 | BJBHT.A9R7 | BLECF_ | 505 | 0x | 01F9 | 8 | RR77 | BY02 | 7 | CR | 3 | 4 | D | 23-24 | SR7 | BY05 | C | 9 | 11-12 | BY02 | E | 4 | 14 | 10 | 1-8 |  | ↑ | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLME.BLETC.10 (01-08) |  | 0
75 | BJBHT.B9R7 | BLECF_ | 345 | 0x | 0159 | 8 | RR77 | BY02 | 7 | CR | 3 | 5 | E | 1-2 | SR7 | BY05 | C | 8 | 1-2 | BY02 | R | 3 | 6 | 3 | 9-16 | Patch cord in the tunnel broken |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.03 (09-16) |  | 1286 | bar: 10pA 2; 10pA 7
76 | BJBHT.A10R7 | BLECF_ | 381 | 0x | 017D | 8 | RR77 | BY02 | 7 | CR | 3 | 6 | E | 3-4 | SR7 | BY05 | C | 8 | 3-4 | BY02 | R | 3 | 7 | 4 | 1-8 |  |  |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1400 BLMbits | CFV-SR7-BLMR.BLETC.04 (01-08) | Check in the tunnel if channel 7 and 8 are mix up
77 | BJBHT.A11R7 | BLECF_ | 428 | 0x | 01AC | 8 | RR77 | BY02 | 7 | CR | 3 | 7 | E | 5-6 | SR7 | BY05 | C | 8 | 5-6 | BY02 | E | 4 | 14 | 10 | 9-16 | Patch cord surface broken | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLME.BLETC.10 (09-16) |  | 0
78 | BJBHT.B11R7 | BLECF_ | 441 | 0x | 01B9 | 7 | RR77 | BY02 | 7 | CR | 3 | 8 | F | 1-2 | SR7 | BY05 | C | 7 | 1-2 | BY02 | R | 3 | 7 | 4 | 9-16 | was wrong conneted on patch |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1400 BLMbits | CFV-SR7-BLMR.BLETC.04 (09-16)
79 | BJBHT.A12R7 | BLECF_ | 160 | 0x | 00A0 | 6 | Arc | BYPLM.A12R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | F | 8 | 7-8 | BY02 | R | 3 | 8 | 5 | 1-8 |  |  |  | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.05 (01-08) |  |  | 1313
80 | BJBHT.A13R7 | BLECF_ | 716 | 0x | 02CC | 6 | Arc | BYPLM.A13R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.05 (09-16) |  | 1402 | bar: noise specta 6
81 | BJBHT.A14R7 | BLECF_ | 44 | 0x | 002C | 6 | Arc | BYPLM.A14R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | F | 10 | 7-8 | BY02 | R | 3 | 9 | 6 | 1-8 |  |  |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 400 BLMbits | CFV-SR7-BLMR.BLETC.06 (01-08) |  | 0
82 | BJBHT.A15R7 | BLECF_ | 264 | 0x | 0108 | 6 | Arc | BYPLM.A15R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | F | 11 | 7-8 | BY02 | R | 3 | 9 | 6 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.06 (09-16)
83 | BJBHT.A16R7 | BLECF_ | 413 | 0x | 019D | 6 | Arc | BYPLM.A16R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | F | 12 | 7-8 | BY02 | R | 3 | 10 | 7 | 1-8 |  |  |  | OK | OK | ↑ | ↑ | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.07 (01-08) | bar: noise specta 3; noise specta 5 to noise specta 6
84 | BJBHT.A17R7 | BLECF_ | 467 | 0x | 01D3 | 6 | Arc | BYPLM.A17R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | G | 7 | 7-8 | BY02 | R | 3 | 10 | 7 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.07 (09-16) |  |  | 1896 | bar: noise specta 1; noise specta 3
85 | BJBHT.A18R7 | BLECF_ | 263 | 0x | 0107 | 6 | Arc | BYPLM.A18R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | G | 8 | 7-8 | BY02 | R | 3 | 11 | 8 | 1-8 |  |  |  | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.08 (01-08)
86 | BJBHT.A19R7 | BLECF_ | 291 | 0x | 0123 | 6 | Arc | BYPLM.A19R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | G | 9 | 7-8 | BY02 | R | 3 | 11 | 8 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.08 (09-16)
87 | BJBHT.A20R7 | BLECF_ | 236 | 0x | 00EC | 6 | Arc | BYPLM.A20R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 |  |  |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.09 (01-08)
88 | BJBHT.A21R7 | BLECF_ | 158 | 0x | 009E | 6 | Arc | BYPLM.A21R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.09 (09-16) |  | 0
89 | BJBHT.A22R7 | BLECF_ | 256 | 0x | 0100 | 6 | Arc | BYPLM.A22R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | G | 12 | 7-8 | BY02 | R | 3 | 14 | 10 | 1-8 |  |  |  | OK | ↑ | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.10 (01-08) | bar: noise specta 3 to noise specta 5
90 | BJBHT.A23R7 | BLECF_ | 65 | 0x | 0041 | 6 | Arc | BYPLM.A23R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | H | 7 | 7-8 | BY02 | R | 3 | 14 | 10 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 400 BLMbits | CFV-SR7-BLMR.BLETC.10 (09-16)
91 | BJBHT.A24R7 | BLECF_ | 152 | 0x | 0098 | 6 | Arc | BYPLM.A24R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  |  |  | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLMR.BLETC.11 (01-08) |  | 0
92 | BJBHT.A25R7 | BLECF_ | 220 | 0x | 00DC | 6 | Arc | BYPLM.A25R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | H | 9 | 7-8 | BY02 | R | 3 | 15 | 11 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.11 (09-16) |  | 0
93 | BJBHT.A26R7 | BLECF_ | 133 | 0x | 0085 | 6 | Arc | BYPLM.A26R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | H | 10 | 7-8 | BY02 | R | 3 | 16 | 12 | 1-8 |  |  |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLMR.BLETC.12 (01-08) |  | 1284
94 | BJBHT.A27R7 | BLECF_ | 138 | 0x | 008A | 6 | Arc | BYPLM.A27R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR7-BLMR.BLETC.12 (09-16) |  | 1320
95 | BJBHT.A28R7 | BLECF_ | 238 | 0x | 00EE | 6 | Arc | BYPLM.A28R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | H | 12 | 7-8 | BY02 | R | 3 | 17 | 13 | 1-8 |  |  |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.13 (01-08)
96 | BJBHT.A29R7 | BLECF_ | 216 | 0x | 00D8 | 6 | Arc | BYPLM.A29R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.13 (09-16)
97 | BJBHT.A30R7 | BLECF_ | 174 | 0x | 00AE | 6 | Arc | BYPLM.A30R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | I | 8 | 7-8 | BY02 | R | 3 | 18 | 14 | 1-8 |  |  |  | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | 10pA 4: 900 BLMbits | CFV-SR7-BLMR.BLETC.14 (01-08)
98 | BJBHT.A31R7 | BLECF_ | 132 | 0x | 0084 | 6 | Arc | BYPLM.A31R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | I | 9 | 7-8 | BY02 | R | 3 | 18 | 14 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR7-BLMR.BLETC.14 (09-16)
99 | BJBHT.A32R7 | BLECF_ | 397 | 0x | 018D | 6 | Arc | BYPLM.A32R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | I | 10 | 7-8 | BY02 | R | 3 | 19 | 15 | 1-8 |  |  |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.15 (01-08)
100 | BJBHT.A33R7 | BLECF_ | 2 | 0x | 0002 | 6 | Arc | BYPLM.A33R7 | 7 | R |  |  |  | 7-8 | SR7 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR7-BLMR.BLETC.15 (09-16)
101 | BJBHT.A34R7 | BLECF_ | 486 | 0x | 01E6 | 6 | Arc | BYPLM.A34R7 | 7 | R |  |  |  | 7-9 | SR7 | BY05 | I | 12 | 7-8 | BY02 | R | 3 | 20 | 16 | 1-8 |  |  |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR7-BLMR.BLETC.16 (01-08) |  | 0
last entry 22/5/08
| Door | [7 empty] | Transformer soldered
[46 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA
[6 empty] | Card number correct | [31 empty] | noise specta 4: < 100 BLMbits; Modulation 4: o.k.; 10pA 4: o.k.
|  |  |  | 0x | 0000 | Card number needs to be checked
|  |  |  | 0x | 0000 | Card number unknown need to be checked in the tunnel | [31 empty] | noise specta 4: 100-300 BLMbits; Modulation 4: Prob. values mod; 10pA 4: to small values 20s
|  | BLECF_ | 656 | Card was exchanged, Data base need to be checked for the correct number | [33 empty] | noise specta 4: > 300 BLMbits; Modulation 4: Prob. Data base; 10pA 4: Prob. to be checked
[49 empty] | > 522 BLMbits | [7 empty] | Flag missing in DB
[47 empty] | n |  | no data
Note on BU3: effinger: No newer Scan possible till right VME is down
Note on BW3: effinger: Repaired week41 to be verified by scan
Note on AA8: effinger: CFC card was not working -> reset -> o.k
Note on AL15: effinger: FID seen 7.10.09
Note on AY16: effinger: To be checked again: in expert application only 1s and 2s!
Note on AJ17: effinger: same situation like 7.10
Note on AL17: effinger: same situation like 7.10
Note on AZ17: effinger: To be checked again: in expert application only ones!
Note on AY18: effinger: To be checked again: in expert application only ones!
Note on AA20: effinger: CFC card was not working -> reset -> o.k
Note on AS20: effinger: CFC-ERROR on ! Repaiered
Note on BB30: effinger: To be verified again!
Note on BG30: jemery: High amplitude and noisy Card exchanged then OK
Note on BJ30: Noisy Card exchanged then OK
Note on AM31: effinger: Level indication from ch1 to 6 : ion found a HV cable where the isolation was defect and tuched the cable tray: repaired with tape : Problem solved ! ->porbably exchange of cable would be good !
Note on BD36: jemery: Phase too low
Note on BC38: jemery: Phase too high (stange data…), next test ok
Note on BW41: effinger: Scan necessary
Note on BC44: jemery: Spare for phase 2
Note on BC45: jemery: Spare for phase 2
Note on BW46: effinger: Scan neccessary
Note on BH47: jemery: Spare for phase 2
Note on BH48: jemery: Spare for phase 2
Note on BJ49: jemery: Spare for phase 2
Note on BJ50: jemery: Spare for phase 2
Note on BW51: effinger: effinger: Scan neccessary
Note on BE52: jemery: Spare for phase 2
Note on BF52: jemery: Spare for phase 2
Note on BG52: jemery: Spare for phase 2
Note on BH52: jemery: Spare for phase 2
Note on BE53: jemery: Spare for phase 2
Note on BF53: jemery: Spare for phase 2
Note on BG53: jemery: Spare for phase 2
Note on BH53: jemery: Spare for phase 2
Note on BC59: jemery: Spare for phase 2
Note on BD59: jemery: Spare for phase 2
Note on BE59: jemery: Spare for phase 2
Note on BF59: jemery: Spare for phase 2
Note on BC60: jemery: Spare for phase 2
Note on BD60: jemery: Spare for phase 2
Note on BE60: jemery: Spare for phase 2
Note on BF60: jemery: Spare for phase 2
Note on BC62: jemery: Spare for phase 2
Note on BC63: jemery: Spare for phase 2
Note on BE69: jemery: Spare for phase 2
Note on BE70: jemery: Spare for phase 2
Note on BI82: jemery: Pobably channels mixed between 7 and 8
Note on AI91: effinger: Russian checked the connection of the fiber in the tunnel and it was not clipped correctly -> o.k
Note on AK91: effinger: CID while last check see LFB
Note on AL91: effinger: FID while last check see LF B
Note on D118: effinger: 565 original number chnaged to 656
Note on BD120: jemery: Spare for phase 2

## Point 8
SR8 | Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA | [7 empty] | Expert Name |  | HV Levels | HV Levels | HV Levels
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | other | Scan | Scan | Scan
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 23.09.09 |  | 07.10.09 |  | 13.10.09 |  | 13.10.09 |  |  |  |  | noise specta 1: 10.10 and 12.10; Modulation 1: 8.10 and 12.10; 10pA 1: 19.10 |  | Comments | 7.9.09 | 2.10.09
1 | BJBHT.A33L8 | BLECF_ | 229 | 0x | 00E5 | 6 | Arc | BYPLM.A33L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | I | 5 | 7-8 | BY02 | L | 1 | 19 | 15 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.15 (09-16) |  | 1427
2 | BJBHT.A32L8 | BLECF_ | 237 | 0x | 00ED | 6 | Arc | BYPLM.A32L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | I | 4 | 7-8 | BY02 | L | 1 | 19 | 15 | 1-8 |  | OK | ↑ | OK | ↑ | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.15 (01-08) |  | 1405 | bar: 10pA 5 to 10pA 6; 10pA 8
3 | BJBHT.A31L8 | BLECF_ | 292 | 0x | 0124 | 6 | Arc | BYPLM.A31L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | I | 3 | 7-8 | BY02 | L | 1 | 18 | 14 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.14 (09-16)
4 | BJBHT.A30L8 | BLECF_ | 257 | 0x | 0101 | 6 | Arc | BYPLM.A30L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | I | 2 | 7-8 | BY02 | L | 1 | 18 | 14 | 1-8 |  | ↑ | OK | ↑ | OK | OK | ↑ | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.14 (01-08) | bar: noise specta 5
5 | BJBHT.A29L8 | BLECF_ | 215 | 0x | 00D7 | 6 | Arc | BYPLM.A29L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | I | 1 | 7-8 | BY02 | L | 1 | 17 | 13 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.13 (09-16)
6 | BJBHT.A28L8 | BLECF_ | 213 | 0x | 00D5 | 6 | Arc | BYPLM.A28L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | H | 6 | 7-8 | BY02 | L | 1 | 17 | 13 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.13 (01-08)
7 | BJBHT.A27L8 | BLECF_ | 275 | 0x | 0113 | 6 | Arc | BYPLM.A27L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | H | 5 | 7-8 | BY02 | L | 1 | 16 | 12 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.12 (09-16)
8 | BJBHT.A26L8 | BLECF_ | 277 | 0x | 0115 | 6 | Arc | BYPLM.A26L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 16 | 12 | 1-8 |  | ↑ | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.12 (01-08) |  | 1404 | bar: noise specta 6
9 | BJBHT.A25L8 | BLECF_ | 247 | 0x | 00F7 | 6 | Arc | BYPLM.A25L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | H | 3 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 | check in tunnel needed | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.11 (09-16)
10 | BJBHT.A24L8 | BLECF_ | 137 | 0x | 0089 | 6 | Arc | BYPLM.A24L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | H | 2 | 7-8 | BY02 | L | 1 | 15 | 11 | 1-8 | check in tunnel needed | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLML.BLETC.11 (01-08)
11 | BJBHT.A23L8 | BLECF_ | 145 | 0x | 0091 | 6 | Arc | BYPLM.A23L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 400 BLMbits | CFV-SR8-BLML.BLETC.10 (09-16) |  | 1319
12 | BJBHT.A22L8 | BLECF_ | 129 | 0x | 0081 | 6 | Arc | BYPLM.A22L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | G | 6 | 7-8 | BY02 | L | 1 | 14 | 10 | 1-8 |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 400 BLMbits | CFV-SR8-BLML.BLETC.10 (01-08) |  | 1412
13 | BJBHT.A21L8 | BLECF_ | 112 | 0x | 0070 | 6 | Arc | BYPLM.A21L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLML.BLETC.09 (09-16) |  | 1403
14 | BJBHT.A20L8 | BLECF_ | 100 | 0x | 0064 | 6 | Arc | BYPLM.A20L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | G | 4 | 7-8 | BY02 | L | 1 | 13 | 9 | 1-8 |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR8-BLML.BLETC.09 (01-08) |  | 1259
15 | BJBHT.A19L8 | BLECF_ | 114 | 0x | 0072 | 6 | Arc | BYPLM.A19L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | G | 3 | 7-8 | BY02 | L | 1 | 11 | 8 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLML.BLETC.08 (09-16)
16 | BJBHT.A18L8 | BLECF_ | 293 | 0x | 0125 | 6 | Arc | BYPLM.A18L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | G | 2 | 7-8 | BY02 | L | 1 | 11 | 8 | 1-8 |  | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.08 (01-08)
17 | BJBHT.A17L8 | BLECF_ | 150 | 0x | 0096 | 6 | Arc | BYPLM.A17L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | G | 1 | 7-8 | BY02 | L | 1 | 10 | 7 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLML.BLETC.07 (09-16)
18 | BJBHT.A16L8 | BLECF_ | 130 | 0x | 0082 | 6 | Arc | BYPLM.A16L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | F | 5 | 7-8 | BY02 | L | 1 | 10 | 7 | 1-8 |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 500 BLMbits | CFV-SR8-BLML.BLETC.07 (01-08)
19 | BJBHT.A15L8 | BLECF_ | 101 | 0x | 0065 | 6 | Arc | BYPLM.A15L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | F | 4 | 7-8 | BY02 | L | 1 | 9 | 6 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR8-BLML.BLETC.06 (09-16)
20 | BJBHT.A14L8 | BLECF_ | 105 | 0x | 0069 | 6 | Arc | BYPLM.A14L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | F | 3 | 7-8 | BY02 | L | 1 | 9 | 6 | 1-8 |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.06 (01-08)
21 | BJBHT.A13L8 | BLECF_ | 99 | 0x | 0063 | 6 | Arc | BYPLM.A13L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 700 BLMbits | CFV-SR8-BLML.BLETC.05 (09-16)
22 | BJBHT.A12L8 | BLECF_ | 712 | 0x | 02C8 | 6 | Arc | BYPLM.A12L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 | check on surface with TB | OK | ↑ | OK | ↑ | OK | ↑ | OK | OK | ↑ | ↑ | ↑ | 10pA 4: 40us: 0 BLMbit | CFV-SR8-BLML.BLETC.05 (01-08) | TC to be excahged
23 | BJBHT.C11L8 | BLECF_ | 95 | 0x | 005F | 6 | UA83 | BY05 | 8 | CL | 2 | 9 | C | 13-14 | SR8 | BY05 | C | 4 | 1-2 | BY02 | L | 1 | 7 | 4 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.04 (09-16) |  | 1275
24 | BJBHT.B11L8 | BLECF_ | 92 | 0x | 005C | 6 | UA83 | BY05 | 8 | CL | 2 | 8 | C | 11-12 | SR8 | BY05 | C | 3 | 11-12 | BY02 | C | 2 | 9 | 6 | 1-8 |  | OK | ↑ |  |  | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMC.BLETC.06 (01-08) | Slava: Expert name missing in MTF | bar: Modulation 7
25 | BJBHT.A11L8 | BLECF_ | 86 | 0x | 0056 | 6 | UA83 | BY05 | 8 | CL | 2 | 7 | C | 9-10 | SR8 | BY05 | C | 3 | 9-10 | BY02 | C | 2 | 8 | 5 | 9-16 | check on surface with TB | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMC.BLETC.05 (09-16) | bar: noise specta 1 to noise specta 6
26 | BJBHT.A10L8 | BLECF_ | 67 | 0x | 0043 | 6 | UA83 | BY05 | 8 | CL | 2 | 6 | C | 7-8 | SR8 | BY05 | C | 3 | 7-8 | BY02 | L | 1 | 7 | 4 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLML.BLETC.04 (01-08)
27 | BJBHT.A9L8 | BLECF_ | 33 | 0x | 0021 | 6 | UA83 | BY05 | 8 | CL | 2 | 5 | C | 5-6 | SR8 | BY05 | C | 3 | 5-6 | BY02 | L | 1 | 6 | 3 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.03 (09-16) | bar: noise specta 1; noise specta 3; noise specta 5
28 | BJBHT.C8L8 | BLECF_ | 224 | 0x | 00E0 | 6 | UA83 | BY05 | 8 | CL | 2 | 4 | C | 3-4 | SR8 | BY05 | C | 3 | 3-4 | BY02 | L | 1 | 6 | 3 | 1-8 |  | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLML.BLETC.03 (01-08)
29 | BJBHT.B8L8 | BLECF_ | 205 | 0x | 00CD | 6 | UA83 | BY05 | 8 | CL | 2 | 3 | C | 1-2 | SR8 | BY05 | C | 3 | 1-2 | BY02 | C | 2 | 8 | 5 | 1-8 |  | OK | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMC.BLETC.05 (01-08)
30 | BJBHT.A8L8 | BLECF_ | 151 | 0x | 0097 | 6 | UA83 | BY05 | 8 | CL | 2 | 2 | B | 23-24 | SR8 | BY05 | C | 2 | 11-12 | BY02 | C | 2 | 7 | 4 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | noise specta 1: n; noise specta 2: n; noise specta 3: n; noise specta 4: n; noise specta 5: n; noise specta 6: n; 10pA 4: 800 BLMbits | CFV-SR8-BLMC.BLETC.04 (09-16) | Jonathan and Ion: check in the tunnel necessary Done!
31 | BJBHT.A7L8 | BLECF_ | 221 | 0x | 00DD | 6 | UA83 | BY05 | 8 | CL | 2 | 1 | B | 21-22 | SR8 | BY05 | C | 2 | 9-10 | BY02 | L | 1 | 5 | 2 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.02 (09-16) |  | 1264 | 1330
32 | BJBHT.B6L8 | BLECF_ | 239 | 0x | 00EF | 7 | UA83 | BY05 | 8 | CL | 1 | 10 | B | 19-20 | SR8 | BY05 | C | 2 | 7-8 | BY02 | L | 1 | 5 | 2 | 1-8 |  | ↑ | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.02 (01-08) | bar: 10pA 1
33 | BJBHT.A6L8 | BLECF_ | 231 | 0x | 00E7 | 1 | UA83 | BY05 | 8 | CL | 1 | 9 | B | 17-18 | SR8 | BY05 | C | 2 | 5-6 | BY02 | C | 2 | 7 | 4 | 1-8 | check on surface with TB | OK | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMC.BLETC.04 (01-08) | bar: noise specta 1
34 | BJBHT.A5L8 | BLECF_ | 240 | 0x | 00F0 | 6 | UA83 | BY05 | 8 | CL | 1 | 8 | B | 15-16 | SR8 | BY05 | C | 2 | 3-4 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.01 (09-16)
35 | BJBHT.C4L8 | BLECF_ | 246 | 0x | 00F6 | 8 | UA83 | BY05 | 8 | CL | 1 | 7 | B | 13-14 | SR8 | BY05 | C | 2 | 1-2 | BY02 | L | 1 | 4 | 1 | 1-8 |  | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLML.BLETC.01 (01-08)
36 | BJBHT.B4L8 | BLECF_ | 248 | 0x | 00F8 | 1 | UA83 | BY05 | 8 | CL | 1 | 6 | B | 11-12 | SR8 | BY05 | C | 1 | 11-12 | BY02 | C | 2 | 6 | 3 | 9-16 | check on surface with TB | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | noise specta 1: n; 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.03 (09-16)
37 | BJBHT.A4L8 | BLECF_ | 243 | 0x | 00F3 | 2 | UA83 | BY05 | 8 | CL | 1 | 5 | B | 9-10 | SR8 | BY05 | C | 1 | 9-10 | BY02 | C | 2 | 6 | 3 | 1-8 | check on surface with TB | ↑ | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | noise specta 1: n; noise specta 2: n; 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.03 (01-08) |  | 1241
38 | BJBHT.A3L8 | BLECF_ | 250 | 0x | 00FA | 8 | UA83 | BY05 | 8 | CL | 1 | 4 | B | 7-8 | SR8 | BY05 | C | 1 | 7-8 | BY02 | C | 2 | 5 | 2 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.02 (09-16)
39 | BJBHT.A2L8 | BLECF_ | 261 | 0x | 0105 | 8 | UA83 | BY05 | 8 | CL | 1 | 3 | B | 5-6 | SR8 | BY05 | C | 1 | 5-6 | BY02 | C | 2 | 5 | 2 | 1-8 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.02 (01-08)
40 | BJBHT.B1L8 | BLECF_ | 269 | 0x | 010D | 5 | UA83 | BY05 | 8 | CL | 1 | 2 | B | 3-4 | SR8 | BY05 | C | 1 | 3-4 | BY02 | C | 2 | 4 | 1 | 9-16 | check on surface with TB | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.01 (09-16)
41 | BJBHT.A1L9 | BLECF_ | 265 | 0x | 0109 | 1 | UA83 | BY05 | 8 | CL | 1 | 1 | B | 1-2 | SR8 | BY05 | C | 1 | 1-2 | BY02 | C | 2 | 4 | 1 | 1-8 |  | OK | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.01 (01-08)
42 | BJBHT.A1R8 | BLECF_ | 78 | 0x | 004E | 1 | UA87 | BY06 | 8 | CR | 1 | 1 | B | 1-2 | SR8 | BY05 | C | 12 | 1-2 | BY02 | C | 2 | 13 | 9 | 1-8 |  | OK | ↑ |  |  | OK | ↑ | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMC.BLETC.09 (01-08) | Jonathan and Ion: check in the tunnel necessary Done! | bar: 10pA 5
43 | BJBHT.B1R8 | BLECF_ | 75 | 0x | 004B | 5 | UA87 | BY06 | 8 | CR | 1 | 2 | B | 3-4 | SR8 | BY05 | C | 12 | 3-4 | BY02 | C | 2 | 13 | 9 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.09 (09-16)
44 | BJBHT.A2R8 | BLECF_ | 70 | 0x | 0046 | 8 | UA87 | BY06 | 8 | CR | 1 | 3 | B | 5-6 | SR8 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.10 (01-08)
45 | BJBHT.A3R8 | BLECF_ | 228 | 0x | 00E4 | 4 | UA87 | BY06 | 8 | CR | 1 | 4 | B | 7-8 | SR8 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.10 (09-16)
46 | BJBHT.A4R8 | BLECF_ | 71 | 0x | 0047 | 7 | UA87 | BY06 | 8 | CR | 1 | 5 | B | 9-10 | SR8 | BY05 | C | 12 | 9-10 | BY02 | C | 2 | 15 | 11 | 1-8 | check in tunnel needed | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.11 (01-08) | Romain & Ewald: removing of the splitter (spare fibre)
47 | BJBHT.B4R8 | BLECF_ | 287 | 0x | 011F | 4 | UA87 | BY06 | 8 | CR | 1 | 6 | B | 11-12 | SR8 | BY05 | C | 12 | 11-12 | BY02 | C | 2 | 15 | 11 | 9-16 | check on surface with TB | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | noise specta 1: n; noise specta 2: n; noise specta 3: n; noise specta 4: n; 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.11 (09-16)
48 | BJBHT.C4R8 | BLECF_ | 278 | 0x | 0116 | 1 | UA87 | BY06 | 8 | CR | 1 | 7 | B | 13-14 | SR8 | BY05 | C | 11 | 1-2 | BY02 | C | 2 | 16 | 12 | 1-8 |  | OK | ↑ |  |  | OK | OK | OK | OK | OK | OK | OK | noise specta 1: n; 10pA 4: 1200 BLMbits | CFV-SR8-BLMC.BLETC.12 (01-08)
49 | BJBHT.D4R8 | BLECF_ | 209 | 0x | 00D1 | 8 | UA87 | BY06 | 8 | CR | 1 | 8 | B | 15-16 | SR8 | BY05 | C | 11 | 3-4 | BY02 | R | 3 | 4 | 1 | 1-8 | check on surface with TB | ↑ | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.01 (01-08)
50 | BJBHT.A5R8 | BLECF_ | 233 | 0x | 00E9 | 6 | UA87 | BY06 | 8 | CR | 1 | 9 | B | 17-18 | SR8 | BY05 | C | 11 | 5-6 | BY02 | R | 3 | 4 | 1 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMR.BLETC.01 (09-16)
51 | BJBHT.A6R8 | BLECF_ | 267 | 0x | 010B | 6 | UA87 | BY06 | 8 | CR | 1 | 10 | B | 19-20 | SR8 | BY05 | C | 11 | 7-8 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMC.BLETC.12 (09-16) |  | 1403 | bar: noise specta 3 to noise specta 5
52 | BJBHT.B6R8 | BLECF_ | 29 | 0x | 001D | 6 | UA87 | BY06 | 8 | CR | 2 | 1 | B | 21-22 | SR8 | BY05 | C | 11 | 9-10 | BY02 | C | 2 | 17 | 13 | 1-8 | check on surface with TB | OK | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | noise specta 4: n; 10pA 4: 1300 BLMbits | CFV-SR8-BLMC.BLETC.13 (01-08)
53 | BJBHT.C6R8 | BLECF_ | 27 | 0x | 001B | 6 | UA87 | BY06 | 8 | CR | 2 | 2 | B | 23-24 | SR8 | BY05 | C | 11 | 11-12 | BY02 | R | 3 | 5 | 2 | 1-8 |  | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.02 (01-08) | bar: noise specta 1 to noise specta 6
54 | BJBHT.A7R8 | BLECF_ | 26 | 0x | 001A | 6 | UA87 | BY06 | 8 | CR | 2 | 3 | C | 1-2 | SR8 | BY05 | C | 10 | 1-2 | BY02 | R | 3 | 5 | 2 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLMR.BLETC.02 (09-16)
55 | BJBHT.A8R8 | BLECF_ | 24 | 0x | 0018 | 6 | UA87 | BY06 | 8 | CR | 2 | 4 | C | 3-4 | SR8 | BY05 | C | 10 | 3-4 | BY02 | C | 2 | 17 | 13 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLMC.BLETC.13 (09-16)
56 | BJBHT.B8R8 | BLECF_ | 25 | 0x | 0019 | 6 | UA87 | BY06 | 8 | CR | 2 | 5 | C | 5-6 | SR8 | BY05 | C | 10 | 5-6 | BY02 | C | 2 | 18 | 14 | 1-8 | check on surface with TB | ↑ | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 400 BLMbits | CFV-SR8-BLMC.BLETC.14 (01-08)
57 | BJBHT.C8R8 | BLECF_ | 127 | 0x | 007F | 6 | UA87 | BY06 | 8 | CR | 2 | 6 | C | 7-8 | SR8 | BY05 | C | 10 | 7-8 | BY02 | R | 3 | 6 | 3 | 1-8 |  | OK | ↑ | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.03 (01-08) | bar: noise specta 1 to noise specta 6
58 | BJBHT.A9R8 | BLECF_ | 80 | 0x | 0050 | 6 | UA87 | BY06 | 8 | CR | 2 | 7 | C | 9-10 | SR8 | BY05 | C | 10 | 9-10 | BY02 | R | 3 | 6 | 3 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.03 (09-16)
59 | BJBHT.A10R8 | BLECF_ | 353 | 0x | 0161 | 6 | UA87 | BY06 | 8 | CR | 2 | 8 | C | 11-12 | SR8 | BY05 | C | 10 | 11-12 | BY02 | R | 3 | 7 | 4 | 1-8 | check on surface with TB | ↑ | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.04 (01-08)
60 | BJBHT.A11R8 | BLECF_ | 6 | 0x | 0006 | 6 | UA87 | BY06 | 8 | CR | 2 | 9 | C | 13-14 | SR8 | BY05 | C | 9 | 1-2 | BY02 | C | 2 | 18 | 14 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMC.BLETC.14 (09-16) | bar: noise specta 3; noise specta 5 to noise specta 6; Modulation 7
61 | BJBHT.B11R8 | BLECF_ | 113 | 0x | 0071 | 6 | UA87 | BY06 | 8 | CR | 2 | 10 | C | 15-16 | SR8 | BY05 | C | 9 | 3-4 | BY02 | C | 2 | 19 | 15 | 1-8 |  | ↑ | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMC.BLETC.15 (01-08) | bar: noise specta 1 to noise specta 6
62 | BJBHT.C11R8 | BLECF_ | 300 | 0x | 012C | 6 | UA87 | BY06 | 8 | CR | 3 | 1 | C | 17-18 | SR8 | BY05 | C | 9 | 5-6 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 1200 BLMbits | CFV-SR8-BLMR.BLETC.04 (09-16) | CH2 => Monitor exchanged. CH15 signal should go to BLMC.BLETC.14 CH15 | 1431
63 | BJBHT.A12R8 | BLECF_ | 272 | 0x | 0110 | 6 | Arc | BYPLM.A12R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | F | 8 | 7-8 | BY02 | R | 3 | 8 | 5 | 1-8 |  | OK | OK |  |  | OK | ↑ | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.05 (01-08)
64 | BJBHT.A13R8 | BLECF_ | 51 | 0x | 0033 | 6 | Arc | BYPLM.A13R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 300 BLMbits | CFV-SR8-BLMR.BLETC.05 (09-16)
65 | BJBHT.A14R8 | BLECF_ | 54 | 0x | 0036 | 6 | Arc | BYPLM.A14R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | F | 10 | 7-8 | BY02 | R | 3 | 9 | 6 | 1-8 | check on surface with TB | ↑ | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 300 BLMbits | CFV-SR8-BLMR.BLETC.06 (01-08) |  | 1404
66 | BJBHT.A15R8 | BLECF_ | 30 | 0x | 001E | 6 | Arc | BYPLM.A15R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | F | 11 | 7-8 | BY02 | R | 3 | 9 | 6 | 9-16 | check on surface with TB | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLMR.BLETC.06 (09-16)
67 | BJBHT.A16R8 | BLECF_ | 142 | 0x | 008E | 6 | Arc | BYPLM.A16R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | F | 12 | 7-8 | BY02 | R | 3 | 10 | 7 | 1-8 |  | ↑ | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLMR.BLETC.07 (01-08)
68 | BJBHT.A17R8 | BLECF_ | 61 | 0x | 003D | 6 | Arc | BYPLM.A17R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | G | 7 | 7-8 | BY02 | R | 3 | 10 | 7 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLMR.BLETC.07 (09-16)
69 | BJBHT.A18R8 | BLECF_ | 148 | 0x | 0094 | 6 | Arc | BYPLM.A18R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | G | 8 | 7-8 | BY02 | R | 3 | 11 | 8 | 1-8 |  | OK | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLMR.BLETC.08 (01-08)
70 | BJBHT.A19R8 | BLECF_ | 15 | 0x | 000F | 6 | Arc | BYPLM.A19R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | G | 9 | 7-8 | BY02 | R | 3 | 11 | 8 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.08 (09-16)
71 | BJBHT.A20R8 | BLECF_ | 294 | 0x | 0126 | 6 | Arc | BYPLM.A20R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 | check on surface with TB | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.09 (01-08) |  | 1405
72 | BJBHT.A21R8 | BLECF_ | 286 | 0x | 011E | 6 | Arc | BYPLM.A21R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.09 (09-16)
73 | BJBHT.A22R8 | BLECF_ | 206 | 0x | 00CE | 6 | Arc | BYPLM.A22R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | G | 12 | 7-8 | BY02 | R | 3 | 14 | 10 | 1-8 | check on surface with TB | OK | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.10 (01-08)
74 | BJBHT.A23R8 | BLECF_ | 270 | 0x | 010E | 6 | Arc | BYPLM.A23R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | H | 7 | 7-8 | BY02 | R | 3 | 14 | 10 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.10 (09-16) | bar: noise specta 6
75 | BJBHT.A24R8 | BLECF_ | 131 | 0x | 0083 | 6 | Arc | BYPLM.A24R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 | check on surface with TB | ↑ | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.11 (01-08)
76 | BJBHT.A25R8 | BLECF_ | 227 | 0x | 00E3 | 6 | Arc | BYPLM.A25R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | H | 9 | 7-8 | BY02 | R | 3 | 15 | 11 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.11 (09-16)
77 | BJBHT.A26R8 | BLECF_ | 253 | 0x | 00FD | 6 | Arc | BYPLM.A26R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | H | 10 | 7-8 | BY02 | R | 3 | 16 | 12 | 1-8 |  | ↑ | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.12 (01-08)
78 | BJBHT.A27R8 | BLECF_ | 208 | 0x | 00D0 | 6 | Arc | BYPLM.A27R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.12 (09-16) | bar: noise specta 4; noise specta 6
79 | BJBHT.A28R8 | BLECF_ | 153 | 0x | 0099 | 6 | Arc | BYPLM.A28R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | H | 12 | 7-8 | BY02 | R | 3 | 17 | 13 | 1-8 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | 10pA 4: 600 BLMbits | CFV-SR8-BLMR.BLETC.13 (01-08)
80 | BJBHT.A29R8 | BLECF_ | 106 | 0x | 006A | 6 | Arc | BYPLM.A29R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.13 (09-16)
81 | BJBHT.A30R8 | BLECF_ | 252 | 0x | 00FC | 6 | Arc | BYPLM.A30R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | I | 8 | 7-8 | BY02 | R | 3 | 18 | 14 | 1-8 |  | ↑ | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.14 (01-08)
82 | BJBHT.A31R8 | BLECF_ | 104 | 0x | 0068 | 6 | Arc | BYPLM.A31R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | I | 9 | 7-8 | BY02 | R | 3 | 18 | 14 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.14 (09-16)
83 | BJBHT.A32R8 | BLECF_ | 271 | 0x | 010F | 6 | Arc | BYPLM.A32R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | I | 10 | 7-8 | BY02 | R | 3 | 19 | 15 | 1-8 | check on surface with TB | OK | OK |  |  | ↑ | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.15 (01-08)
84 | BJBHT.A33R8 | BLECF_ | 225 | 0x | 00E1 | 6 | Arc | BYPLM.A33R8 | 8 | R |  |  |  | 7-8 | SR8 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.15 (09-16) |  | 1422
85 | BJBHT.A34R8 | BLECF_ | 297 | 0x | 0129 | 6 | Arc | BYPLM.A34R8 | 8 | R |  |  |  | 7-9 | SR8 | BY05 | I | 12 | 7-8 | BY02 | R | 3 | 20 | 16 | 1-8 |  | ↑ | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [32 empty] | CFV-SR8-BLMR.BLETC.16 (01-08) | bar: noise specta 2; noise specta 5 to noise specta 6
last entry 14/4/08
Transformer soldered
[46 empty] | noise specta | [7 empty] | Modulation | [7 empty] | 10pA
[6 empty] | Card number correct | [31 empty] | noise specta 4: < 100 BLMbits; Modulation 4: o.k.; 10pA 4: o.k.
|  |  |  | 0x | 0000 | Card number needs to be checked
|  |  |  | 0x | 0000 | Card number unknown need to be checked in the tunnel | [31 empty] | noise specta 4: 100-300 BLMbits; Modulation 4: Prob. values mod; 10pA 4: to small values 20s
|  | BLECF_ | 656 | Card was exchanged, Data base need to be checked for the correct number | [33 empty] | noise specta 4: > 300 BLMbits; Modulation 4: Prob. Data base; 10pA 4: to high values 20s
[49 empty] | > 522 BLMbits | [7 empty] | Flag missing in DB | [7 empty] | Prob. to be checked
[47 empty] | n |  | no data
Note on BV3: effinger: repaired week 41 scan needed to be verified
Note on AJ16: effinger: ERRC seen at check 7.10.09
Note on BI29: jemery: No expert name
Note on AJ32: effinger: ERRC seen at check 7.10.09
Note on BC35: jemery: Signal a bit low; Check in the tunnel, all is connected correctly . Ch1 gives a bit smaller signal with the battery than ch2 (probably ADC)
Note on BN40: effinger: 40us: 1000BLMbit jumps seen while check, Romain verfified in the tunnel nothing special seen , reset done all seems to be o.k
Note on BC48: jemery: Small signal amplitude. Chamber not connected? Checked in the tunnel (21.10.09): SEM was not connected, and also connected on the HV box for IC. All working and corrected now!
Note on Z52: effinger: Splitter used!
Note on BL60: effinger: While checking 1 channel went negative
Note on BI66: jemery: Missing signal (BLMEI.11R8.B1I23_MBB)
Note on BD68: jemery: Phase low. Noise on the expert. Monitor exchanged 16 oct 2009
Note on BI68: jemery: No expert name….. The signal should go to BLMC.BLETC.14
Note on D102: effinger: 565 original number chnaged to 656
Note on BD104: jemery: Spare for phase 2

## all problems
| Tunnel - position | [13 empty] | Surface position | [22 empty] | LEVEL | [7 empty] | HV Levels | HV Levels | HV Levels | HV Levels | noise specta | [7 empty] | Modulation | [7 empty] | 10pA
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | ERRA | ERRB | ERRA | ERRB | ERRA | ERRB | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Scan | Scan | Scan | Scan | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | other
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 21.09.09 |  | 13.10.09 |  |  |  | 13.10.09 | [12 empty] | 3.3.09 | 2.10.09 | 9.10.09 | 12.10.09 | Modulation 1: 8.10 and 12.10 | Comments
32 | BJBHT.A6L1 | BLECF_ | 638 | 0x | 027E | 6 | RR13 | BY02 | 1 | CL | 1 | 10 | A | 19-20 | SR1 | BY05 | C | 2 | 7-8 | BY02 | L | 1 | 5 | 2 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [9 empty] | 1299 | [26 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 3; Modulation 8 to 10pA 8
44 | BJBHT.A2R1 | BLECF_ | 501 | 0x | 01F5 | 8 | RR17 | BY02 | 1 | CR | 1 | 3 | A | 5-6 | SR1 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 6 to 10pA 8
45 | BJBHT.A3R1 | BLECF_ | 636 | 0x | 027C | 5 | RR17 | BY02 | 1 | CR | 1 | 4 | A | 7-8 | SR1 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 6 to 10pA 8
49 | BJBHT.A5R1 | BLECF_ | 437 | 0x | 01B5 | 1 | RR17 | BY02 | 1 | CR | 1 | 8 | A | 15-16 | SR1 | BY05 | C | 11 | 3-4 | BY02 | C | 2 | 16 | 12 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1; Modulation 8
24 | BJBHT.B11L2 | BLECF_ | 343 | 0x | 0157 | 6 | UA23 | BY02 | 2 | CL | 3 | 1 | C | 17-18 | SR2 | BY05 | C | 4 | 5-6 | BY02 | C | 2 | 10 | 7 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: Expert name missing in MTF | bar: Modulation 7 to Modulation 8
64 | BJBHT.B11R2 | BLECF_ | 627 | 0x | 0273 | 6 | UA27 | BY03 | 2 | CR | 2 | 10 | C | 15-16 | SR2 | BY05 | C | 9 | 3-4 | BY02 | C | 2 | 19 | 15 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: Expert name missing in MTF | bar: Modulation 7 to Modulation 8
11 | BJBHT.A23L3 | BLECF_ | 730 | 0x | 02DA | 6 | Arc | BYPLM.A23L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Ewald and Romain: checking for GND Loop or bad connector | bar: Modulation 8
31 | BJBHT.A7L3 | BLECF_ | 637 | 0x | 027D | 1 | UJ33 | BY02 | 3 | L | 1 | 10 | B | 19-20 | SR3 | BY05 | C | 2 | 7-8 | BY02 | C | 2 | 7 | 4 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary (higher amp and 1 missing) | bar: Modulation 3; Modulation 6; Modulation 8
46 | BJBHT.D5R3 | BLECF_ | 393 | 0x | 0189 | 2 | UJ33 | BY03 | 3 | R | 1 | 6 | C | 23-24 | SR3 | BY05 | C | 4 | 11-12 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Cross talk: no action can be done | bar: Modulation 8
47 | BJBHT.A6R3 | BLECF_ | 541 | 0x | 021D | 4 | UJ33 | BY03 | 3 | R | 1 | 7 | D | 1-2 | SR3 | BY05 | C | 5 | 1-2 | BY02 | C | 2 | 15 | 11 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Cross talk: no action can be done | bar: Modulation 8
48 | BJBHT.B6R3 | BLECF_ | 341 | 0x | 0155 | 4 | UJ33 | BY03 | 3 | R | 1 | 8 | D | 3-4 | SR3 | BY05 | C | 5 | 3-4 | BY02 | C | 2 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | Cross talk: no action can be done | bar: Modulation 8
49 | BJBHT.C6R3 | BLECF_ | 339 | 0x | 0153 | 6 | UJ33 | BY03 | 3 | R | 1 | 9 | D | 5-6 | SR3 | BY05 | C | 5 | 5-6 | BY02 | R | 3 | 5 | 2 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Cross talk: no action can be done | bar: Modulation 8
0 | BJBHT.A7R3 | BLECF_ | 367 | 0x | 016F | 1 | UJ33 | BY03 | 3 | R | 1 | 10 | D | 7-8 | SR3 | BY05 | C | 5 | 7-8 | BY02 | C | 2 | 16 | 12 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 1321 | [26 empty] | Cross talk: no action can be done | bar: Modulation 2; Modulation 8
51 | BJBHT.B7R3 | BLECF_ | 709 | 0x | 02C5 | 7 | UJ33 | BY03 | 3 | R | 2 | 1 | D | 9-10 | SR3 | BY05 | C | 5 | 9-10 | BY02 | R | 3 | 5 | 2 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 1321 | [26 empty] | Cross talk: no action can be done | bar: Modulation 8
52 | BJBHT.A8R3 | BLECF_ | 502 | 0x | 01F6 | 6 | UJ33 | BY03 | 3 | R | 2 | 2 | D | 11-12 | SR3 | BY05 | C | 5 | 11-12 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Cross talk: no action can be done | bar: Modulation 8
53 | BJBHT.B8R3 | BLECF_ | 183 | 0x | 00B7 | 6 | UJ33 | BY03 | 3 | R | 2 | 3 | D | 13-14 | SR3 | BY05 | C | 6 | 1-2 | BY02 | R | 3 | 6 | 3 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Cross talk: no action can be done | bar: Modulation 8
57 | BJBHT.A11R3 | BLECF_ | 562 | 0x | 0232 | 12 | UJ33 | BY03 | 3 | R | 2 | 7 | D | 21-22 | SR3 | BY05 | C | 6 | 9-10 | BY02 | C | 2 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1573 | [27 empty] | Cross talk: no action can be done | bar: Modulation 8
58 | BJBHT.B11R3 | BLECF_ | 459 | 0x | 01CB | 7 | UJ33 | BY03 | 3 | R | 2 | 8 | D | 23-24 | SR3 | BY05 | C | 6 | 11-12 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Cross talk: no action can be done | bar: Modulation 8
67 | BJBHT.A20R3 | BLECF_ | 523 | 0x | 020B | 6 | Arc | BYPLM.A20R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 3; Modulation 5; Modulation 8
68 | BJBHT.A21R3 | BLECF_ | 185 | 0x | 00B9 | 6 | Arc | BYPLM.A21R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 0 | [26 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 5; Modulation 8
71 | BJBHT.A24R3 | BLECF_ | 309 | 0x | 0135 | 6 | Arc | BYPLM.A24R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 2; Modulation 8
74 | BJBHT.A27R3 | BLECF_ | 519 | 0x | 0207 | 6 | Arc | BYPLM.A27R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 5; Modulation 8
75 | BJBHT.A28R3 | BLECF_ | 448 | 0x | 01C0 | 6 | Arc | BYPLM.A28R3 | 3 | R |  |  |  | 6-7 | SR3 | BY05 | H | 12 | 6-7 | BY02 | R | 3 | 17 | 13 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 0 | [26 empty] | Jonathan and Ion: check in the tunnel necessary Romain and fiber connection 6-7 or 7-8 needs to be verified | bar: Modulation 6; Modulation 8
76 | BJBHT.A29R3 | BLECF_ | 489 | 0x | 01E9 | 6 | Arc | BYPLM.A29R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 4; Modulation 6; Modulation 8
80 | BJBHT.A33R3 | BLECF_ | 453 | 0x | 01C5 | 6 | Arc | BYPLM.A33R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1; Modulation 8
81 | BJBHT.A34R3 | BLECF_ | 109 | 0x | 006D | 6 | Arc | BYPLM.A34R3 | 3 | R |  |  |  | 6-7 | SR3 | BY05 | I | 12 | 6-7 | BY02 | R | 3 | 20 | 16 | 1-8 |  | OK | OK | OK |  |  |  | OK | ↑ | OK | ↑ | ↑ | [8 empty] | 0 | 0 | [26 empty] | Romain & Ewald: LF in B fiber connection need to be checked | bar: Modulation 8
8 | BJBHT.A26L4 | BLECF_ | 318 | 0x | 013E | 6 | Arc | BYPLM.A26L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 6; Modulation 8
24 | BJBHT.A11L4 | BLECF_ | 643 | 0x | 0283 | 6 | UA43 | BY12 | 4 | CL | 1 | 8 | A | 15-16 | SX4 | BY05 | C | 2 | 3-4 | BY02 | L | 1 | 7 | 4 | 1-8 | Fibre missing, check surface TB, PM | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: Expert name missing in MTF | bar: Modulation 7 to Modulation 8
29 | BJBHT.A6L4 | BLECF_ | 157 | 0x | 009D | 6 | UA43 | BY12 | 4 | CL | 1 | 3 | A | 5-6 | SX4 | BY05 | C | 1 | 5-6 | BY02 | L | 1 | 4 | 1 | 9-16 |  | OK | OK | ↑ | OK |  |  | OK | ↑ | ↑ | OK | ↑ | [8 empty] | 0 | 1292 | [26 empty] | Chris: TC card to be checked | bar: Modulation 8
39 | BJBHT.A11R4 | BLECF_ | 10 | 0x | 000A | 6 | UA47 | BY09 | 4 | CR | 1 | 8 | A | 15-16 | SX4 | BY05 | C | 11 | 3-4 | BY02 | R | 3 | 7 | 4 | 1-8 | wrong C no, check tunnel | ↑ | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1399 | [27 empty] | Slava: Expert name missing in MTF | bar: Modulation 7 to Modulation 8
21 | BJBHT.A13L5 | BLECF_ | 640 | 0x | 0280 | 6 | Arc | BYPLM.A13L5 | 5 | L |  |  |  | 7-8 | SR5 | BY05 | F | 2 | 7-8 | BY02 | L | 1 | 8 | 5 | 9-16 | Test in tunnel needed! | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: Expert name missing in MTF | bar: Modulation 8
25 | BJBHT.B10L5 | BLECF_ | 14 | 0x | 000E | 6 | RR53 | BY02 | 5 | CL | 2 | 7 | B | 9-10 | SR5 | BY05 | C | 3 | 9-10 | BY02 | L | 1 | 7 | 4 | 1-8 |  | ↑ | OK | ↑ | OK |  |  | OK | OK | ↑ | OK | ↑ | [36 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 2; Modulation 8
35 | BJBHT.C4L5 | BLECF_ | 356 | 0x | 0164 | 6 | RR53 | BY02 | 5 | CL | 1 | 7 | A | 13-14 | SR5 | BY05 | C | 2 | 1-2 | BY02 | L | 1 | 4 | 1 | 1-8 |  | OK | OK | ↑ | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 1; Modulation 8
60 | BJBHT.B11R5 | BLECF_ | 603 | 0x | 025B | 6 | RR57 | BY02 | 5 | CR | 2 | 9 | B | 13-14 | SR5 | BY05 | C | 9 | 1-2 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 7 to Modulation 8
62 | BJBHT.A13R5 | BLECF_ | 728 | 0x | 02D8 | 6 | Arc | BYPLM.A13R5 | 5 | R |  |  |  | 7-8 | SR5 | BY05 | F | 9 | 7-8 | BY02 | R | 3 | 8 | 5 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: Expert name missing in MTF | bar: Modulation 7 to Modulation 8
23 | UD62 | BLECF_ | 187 | 0x | 00BB | 8 | UJ63 | BY03 | 6 | CL | 3 | 1 | B | 17-18 | SR6 | BY05 | C | 4 | 5-6 | BY02 | C | 2 | 11 | 8 | 1-8 | Power loss could be checked | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 0 | 1994 | up o.k. down not o.k | up o.k. down not o.k | [24 empty] | Ewald and Ion: Retesting of HV with Expert app. And evt. check in tunnel | bar: Modulation 8
26 | BJBHT.A11L6 | BLECF_ | 108 | 0x | 006C | 6 | UJ63 | BY03 | 6 | CL | 2 | 8 | B | 11-12 | SR6 | BY05 | C | 3 | 11-12 | BY02 | L | 1 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Slava: Expert name missing in MTF | bar: Modulation 7 to Modulation 8
51 | BJBHT.H4R6 | BLECF_ | 45 | 0x | 002D | 3 | UJ67 | BY03 | 6 | CR | 1 | 8 | A | 15-16 | SR6 | BY05 | C | 11 | 3-4 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1; Modulation 8
52 | BJBHT.DD | [5 empty] | UJ67 | BY03 | [65 empty] | Ewald and Ion: Testing of the LHCBLM-DD system
52 | BJBHT.DD | [5 empty] | UJ63 | BY03 | [65 empty] | Ewald and Ion: Testing of the LHCBLM-DD system
61 | BJBHT.A11R6 | BLECF_ | 72 | 0x | 0048 | 6 | UJ67 | BY03 | 6 | CR | 2 | 8 | B | 11-12 | SR6 | BY05 | C | 10 | 11-12 | BY02 | R | 3 | 6 | 3 | 9-16 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1321 | 1324 | [26 empty] | Jonathan and Ion: check in the tunnel necessary
62 | TD68.1 | BLECF_ | 391 | 0x | 0187 | 8 | UJ67 | BY03 | 6 | CR | 2 | 9 | B | 13-14 | SR6 | BY05 | C | 9 | 1-2 | BY02 | C | 2 | 19 | 15 | 1-8 |  | ↑ | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [8 empty] | 1406 | [27 empty] | Slava: Expert name missing in MTF | bar: Modulation 6; Modulation 8
63 | TD68.2 | BLECF_ | 56 | 0x | 0038 | 8 | UJ67 | BY03 | 6 | CR | 2 | 10 | B | 15-16 | SR6 | BY05 | C | 9 | 3-4 | BY02 | C | 2 | 19 | 15 | 9-16 |  | OK | ↑ | OK | OK |  |  | OK | OK | ↑ | OK | ↑ | [36 empty] | Ewald and Romain: checking for GND Loop or bad connector | bar: Modulation 8
64 | UD68 | BLECF_ | 82 | 0x | 0052 | 8 | UJ67 | BY03 | 6 | CR | 3 | 1 | B | 17-18 | SR6 | BY05 | C | 9 | 5-6 | BY02 | C | 2 | 20 | 16 | 1-8 |  | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [36 empty] | Ewald and Raymond: disconnecting broken SEM under the DUMP | bar: Modulation 8
13 | BJBHT.A21L7 | BLECF_ | 87 | 0x | 0057 | 6 | Arc | BYPLM.A21L7 | 7 | L |  |  |  | 7-8 | SR7 | BY05 | G | 5 | 7-8 | BY02 | L | 1 | 13 | 9 | 9-16 |  | OK | ↑ | OK | ↑ | OK | ↑ | OK | OK | ↑ | OK | ↑ | [8 empty] | 1403 | [27 empty] | Chris: TC card to be checked | bar: Modulation 8
25 | BJBHT.A10L7 | BLECF_ | 544 | 0x | 0220 | 8 | RR73 | BY01 | 7 | CL | 3 | 6 | E | 3-4 | SR7 | BY05 | C | 5 | 3-4 | BY02 | L | 1 | 7 | 4 | 1-8 |  | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Ewald & Ion: Card exchange due to noise problems | bar: noise specta 1 to noise specta 8; Modulation 8
31 | BJBHT.A7L7 | BLECF_ | 411 | 0x | 019B | 2 | RR73 | BY01 | 7 | CL | 2 | 10 | D | 15-16 | SR7 | BY05 | C | 4 | 3-4 | BY02 | E | 4 | 4 | 1 | 1-8 |  | OK | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [8 empty] | 0 | 1276 | [26 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 2; Modulation 8
33 | BJBHT.H6L7 | BLECF_ | 118 | 0x | 0076 | 4 | RR73 | BY01 | 7 | CL | 2 | 8 | D | 11-12 | SR7 | BY05 | C | 3 | 11-12 | BY02 | C | 2 | 11 | 8 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1; Modulation 8
39 | BJBHT.B6L7 | BLECF_ | 682 | 0x | 02AA | 7 | RR73 | BY01 | 7 | CL | 2 | 2 | C | 23-24 | SR7 | BY05 | C | 2 | 11-12 | BY02 | C | 2 | 8 | 5 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 1; Modulation 8
40 | BJBHT.A6L7 | BLECF_ | 465 | 0x | 01D1 | 7 | RR73 | BY01 | 7 | CL | 2 | 1 | C | 21-22 | SR7 | BY05 | C | 2 | 9-10 | BY02 | C | 2 | 8 | 5 | 1-8 |  | ↑ | OK | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | [10 empty] | 1331 | [25 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 1; Modulation 8
42 | BJBHT.D5L7 | BLECF_ | 94 | 0x | 005E | 6 | RR73 | BY01 | 7 | CL | 1 | 9 | C | 17-18 | SR7 | BY05 | C | 2 | 5-6 | BY02 | C | 2 | 7 | 4 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 6; Modulation 8
43 | BJBHT.C5L7 | BLECF_ | 273 | 0x | 0111 | 6 | RR73 | BY01 | 7 | CL | 1 | 8 | C | 15-16 | SR7 | BY05 | C | 2 | 3-4 | BY02 | C | 2 | 7 | 4 | 1-8 |  | OK | OK | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 6; Modulation 8
44 | BJBHT.B5L7 | BLECF_ | 590 | 0x | 024E | 8 | RR73 | BY01 | 7 | CL | 1 | 7 | C | 13-14 | SR7 | BY05 | C | 2 | 1-2 | BY02 | C | 2 | 6 | 3 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 8
45 | BJBHT.A5L7 | BLECF_ | 1 | 0x | 0001 | 8 | RR73 | BY01 | 7 | CL | 1 | 6 | C | 11-12 | SR7 | BY05 | C | 1 | 11-12 | BY02 | C | 2 | 6 | 3 | 1-8 |  | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 8
47 | BJBHT.D4L6 | BLECF_ | 445 | 0x | 01BD | 6 | RR73 | BY01 | 7 | CL | 1 | 4 | C | 7-8 | SR7 | BY05 | C | 1 | 7-8 | BY02 | C | 2 | 5 | 2 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [8 empty] | 0 | [27 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 3 to Modulation 6; Modulation 8
48 | BJBHT.C4L6 | BLECF_ | 369 | 0x | 0171 | 6 | RR73 | BY01 | 7 | CL | 1 | 3 | C | 5-6 | SR7 | BY05 | C | 1 | 5-6 | BY02 | C | 2 | 5 | 2 | 1-8 |  | ↑ | OK | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | [9 empty] | 1302 | [26 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 3 to Modulation 6; Modulation 8
53 | BJBHT.C4R7 | BLECF_ | 351 | 0x | 015F | 6 | RR77 | BY02 | 7 | CR | 1 | 3 | C | 5-6 | SR7 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | OK | OK | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 1 to Modulation 4; Modulation 8
54 | BJBHT.D4R7 | BLECF_ | 431 | 0x | 01AF | 6 | RR77 | BY02 | 7 | CR | 1 | 4 | C | 7-8 | SR7 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 1 to Modulation 4; Modulation 8
56 | BJBHT.A5R7 | BLECF_ | 412 | 0x | 019C | 8 | RR77 | BY02 | 7 | CR | 1 | 6 | C | 11-12 | SR7 | BY05 | C | 12 | 11-12 | BY02 | C | 2 | 15 | 11 | 1-8 |  | OK | ↑ | ↑ | OK | ↑ | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 1; Modulation 8
57 | BJBHT.B5R7 | BLECF_ | 446 | 0x | 01BE | 8 | RR77 | BY02 | 7 | CR | 1 | 7 | C | 13-14 | SR7 | BY05 | C | 11 | 1-2 | BY02 | C | 2 | 15 | 11 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 1; Modulation 8
63 | BJBHT.C6R7 | BLECF_ | 350 | 0x | 015E | 5 | RR77 | BY02 | 7 | CR | 2 | 3 | D | 1-2 | SR7 | BY05 | C | 10 | 1-2 | BY02 | C | 2 | 18 | 14 | 1-8 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 3; Modulation 8
64 | BJBHT.D6R7 | BLECF_ | 81 | 0x | 0051 | 5 | RR77 | BY02 | 7 | CR | 2 | 4 | D | 3-4 | SR7 | BY05 | C | 10 | 3-4 | BY02 | C | 2 | 18 | 14 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Spare channels: Phase 2 | bar: Modulation 3; Modulation 8
76 | BJBHT.A10R7 | BLECF_ | 381 | 0x | 017D | 8 | RR77 | BY02 | 7 | CR | 3 | 6 | E | 3-4 | SR7 | BY05 | C | 8 | 3-4 | BY02 | R | 3 | 7 | 4 | 1-8 |  |  |  | ↑ | OK | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Check in the tunnel if channel 7 and 8 are mix up | bar: Modulation 7 to Modulation 8
22 | BJBHT.A12L8 | BLECF_ | 98 | 0x | 0062 | 6 | Arc | BYPLM.A12L8 | 8 | L |  |  |  | 7-8 | SR8 | BY05 | F | 1 | 7-8 | BY02 | L | 1 | 8 | 5 | 1-8 | check on surface with TB | OK | ↑ | OK | ↑ | OK | ↑ | OK | OK | ↑ | ↑ | ↑ | [36 empty] | Chris: TC card to be checked | bar: Modulation 8
24 | BJBHT.B11L8 | BLECF_ | 92 | 0x | 005C | 6 | UA83 | BY05 | 8 | CL | 2 | 8 | C | 11-12 | SR8 | BY05 | C | 3 | 11-12 | BY02 | C | 2 | 9 | 6 | 1-8 |  | OK | ↑ |  |  | ↑ | OK | OK | OK | OK | OK | OK | [36 empty] | Slava: Expert name missing in MTF | bar: Modulation 7 to Modulation 8
46 | BJBHT.A4R8 | BLECF_ | 71 | 0x | 0047 | 7 | UA87 | BY06 | 8 | CR | 1 | 5 | B | 9-10 | SR8 | BY05 | C | 12 | 9-10 | BY02 | C | 2 | 15 | 11 | 1-8 | check in tunnel needed | OK | OK |  |  | OK | OK | OK | OK | OK | OK | OK | [36 empty] | Romain & Ewald: removing of the splitter (spare fibre) | bar: Modulation 8
62 | BJBHT.C11R8 | BLECF_ | 300 | 0x | 012C | 6 | UA87 | BY06 | 8 | CR | 3 | 1 | C | 17-18 | SR8 | BY05 | C | 9 | 5-6 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [8 empty] | 1431 | [27 empty] | Slava: Expert name missing in MTF | bar: Modulation 2; Modulation 7 to Modulation 8
Note on AV3: effinger: Repair 9beginning week 41 done by Ion scan necessary to vrrify
Note on BI5: effinger: Lower phase value -> Johnatan need s to check
Note on AM6: effinger: Cable repaired bt I,R and R (week 41)
Note on BL6: jemery: Database or connetion problem
Note on BR6: effinger: 40us->goes to 0
Note on BS6: effinger: 40us->goes to 0
Note on BS7: effinger: 40us->goes to 0
Note on BT7: effinger: 40us->goes to 0
Note on BG8: effinger: Lower phase value -> Johnatan need s to check
Note on AH10: effinger: LF on both cahnnels, after reset with HV o.k.!! 22.9.09
Note on BM10: jemery: MTF entry missing: Babara momitors
Note on BM11: jemery: MTF entry missing: Babara momitors
Note on AQ13: effinger: Ch 5 goes every 20 seconds to 0 all the rest of the time it is working fine, even the runsum 11 is perfect at 1000 BLMbits
Note on BI14: jemery: To high modulation signal
Note on BL14: jemery: One monitor missing out of 2!
Note on BN15: jemery: Cross talk?!
Note on BN16: jemery: Cross talk?!
Note on BN17: jemery: Cross talk?!
Note on BN18: jemery: Cross talk?!
Note on BH19: jemery: Cross talk?!
Note on BN19: jemery: Cross talk?!
Note on AA20: effinger: CFC-Card changed because of very low laser power and patch cord changed because of high attenuation
Note on BN20: jemery: Cross talk?!
Note on BN21: jemery: Cross talk?!
Note on BN22: jemery: Cross talk?!
Note on AM23: effinger: Cable will be replace (800m) 14.10.09
Note on BN23: jemery: Cross talk?!
Note on AN24: effinger: Very high DAC value 37x
Note on BN24: jemery: Cross talk?!
Note on BI25: jemery: Higher amplitude and smaller phase
Note on BK25: jemery: Higher amplitude and smaller phase
Note on AI26: effinger: LF fibre problem ! Is repaired
Note on BK26: jemery: Higher amplitude and smaller phase
Note on BH27: jemery: Higher amplitude and smaller phase
Note on BK28: jemery: Higher amplitude and smaller phase
Note on AA29: effinger: in the tunnel with TB o.k. --> Fibre broken tunnel to surface
Note on AH29: effinger: LF a&B fibre repaired
Note on BL29: jemery: Higher amplitude and smaller phase
Note on BJ30: jemery: Higher amplitude and smaller phase
Note on BL30: jemery: Higher amplitude and smaller phase
Note on BG31: jemery: Higher amplitude and smaller phase
Note on AA32: effinger: in the tunnel with TB o.k. --> Fibre broken tunnel to surface
Note on BL34: jemery: Higher amplitude
Note on BM35: jemery: Monitor missing in MTF
Note on BM37: jemery: Monitor missing in MTF
Note on BN39: jemery: Unconnected monitor
Note on BH40: jemery: Lower phase
Note on BG41: jemery: Strange signal. Different amplitude and phase
Note on BM42: jemery: Missing expert name
Note on BN42: jemery: Expert name exist, but should be in ch 15
Note on BM43: jemery: Missing monitor
Note on AH45: effinger LF A&B 8.9.09 ! O.k 23.9.09
Note on BM46: jemery: Missing expert name
Note on BG47: jemery: Low amplitude
Note on BK50: jemery: Amplitude low phase higher
Note on BL51: jemery: Missing monitor
Note on AT52: effinger: CFC-ERROR
Note on AJ55: effinger: same situation like 7.10
Note on AL55: effinger: same situation like 7.10
Note on BK56: jemery: High amplitude and noisy Card exchanged then OK
Note on BN56: Noisy Card exchanged then OK
Note on BH57: jemery: Phase too low
Note on BG58: jemery: Phase too high (stange data…), next test ok
Note on BG59: jemery: Spare for phase 2
Note on BG60: jemery: Spare for phase 2
Note on BL61: jemery: Spare for phase 2
Note on BL62: jemery: Spare for phase 2
Note on BN63: jemery: Spare for phase 2
Note on BN64: jemery: Spare for phase 2
Note on BI65: jemery: Spare for phase 2
Note on BJ65: jemery: Spare for phase 2
Note on BK65: jemery: Spare for phase 2
Note on BL65: jemery: Spare for phase 2
Note on BI66: jemery: Spare for phase 2
Note on BJ66: jemery: Spare for phase 2
Note on BK66: jemery: Spare for phase 2
Note on BL66: jemery: Spare for phase 2
Note on BG67: jemery: Spare for phase 2
Note on BH67: jemery: Spare for phase 2
Note on BI67: jemery: Spare for phase 2
Note on BJ67: jemery: Spare for phase 2
Note on BG68: jemery: Spare for phase 2
Note on BH68: jemery: Spare for phase 2
Note on BI68: jemery: Spare for phase 2
Note on BJ68: jemery: Spare for phase 2
Note on BG69: jemery: Spare for phase 2
Note on BG70: jemery: Spare for phase 2
Note on BI71: jemery: Spare for phase 2
Note on BI72: jemery: Spare for phase 2
Note on BM73: jemery: Pobably channels mixed between 7 and 8
Note on BM76: jemery: No expert name
Note on Z77: effinger: Splitter used!
Note on BH78: jemery: Phase low. Noise on the expert.
Note on BM78: jemery: No expert name

## Problems with tunnel access
| Tunnel - position | [13 empty] | Surface position | [16 empty] | LEVEL | [7 empty] | Modulation
| HV box | CFC-Card |  |  |  |  | CFC - Position | [5 empty] | Patch |  | Optical patch position |  |  |  |  | VME-TC position | [5 empty] | Comment | LF A | LF B | ERRC | CID | FID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | other
Pos. | position | No. |  | Hex. |  | Ch | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Bldg. | Crate |  |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | 13.10.09 |  |  |  |  | Modulation 1: 8.10 and 12.10 | Comments
32 | BJBHT.A6L1 | BLECF_ | 638 | 0x | 027E | 6 | RR13 | BY02 | 1 | CL | 1 | 10 | A | 19-20 | SR1 | BY05 | C | 2 | 7-8 | BY02 | L | 1 | 5 | 2 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 3
44 | BJBHT.A2R1 | BLECF_ | 501 | 0x | 01F5 | 8 | RR17 | BY02 | 1 | CR | 1 | 3 | A | 5-6 | SR1 | BY05 | C | 12 | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 6 to Modulation 8
45 | BJBHT.A3R1 | BLECF_ | 636 | 0x | 027C | 5 | RR17 | BY02 | 1 | CR | 1 | 4 | A | 7-8 | SR1 | BY05 | C | 12 | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 6 to Modulation 8
49 | BJBHT.A5R1 | BLECF_ | 437 | 0x | 01B5 | 1 | RR17 | BY02 | 1 | CR | 1 | 8 | A | 15-16 | SR1 | BY05 | C | 11 | 3-4 | BY02 | C | 2 | 16 | 12 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1
11 | BJBHT.A23L3 | BLECF_ | 730 | 0x | 02DA | 6 | Arc | BYPLM.A23L3 | 3 | L |  |  |  | 7-8 | SR3 | BY05 | H | 1 | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Ewald and Romain: checking for GND Loop or bad connector | bar: LEVEL 5
31 | BJBHT.A7L3 | BLECF_ | 637 | 0x | 027D | 1 | UJ33 | BY02 | 3 | L | 1 | 10 | B | 19-20 | SR3 | BY05 | C | 2 | 7-8 | BY02 | C | 2 | 7 | 4 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary (higher amp and 1 missing) | bar: Modulation 3; Modulation 6
67 | BJBHT.A20R3 | BLECF_ | 523 | 0x | 020B | 6 | Arc | BYPLM.A20R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 10 | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 3; Modulation 5
68 | BJBHT.A21R3 | BLECF_ | 185 | 0x | 00B9 | 6 | Arc | BYPLM.A21R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | G | 11 | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 5
71 | BJBHT.A24R3 | BLECF_ | 309 | 0x | 0135 | 6 | Arc | BYPLM.A24R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 8 | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 2
74 | BJBHT.A27R3 | BLECF_ | 519 | 0x | 0207 | 6 | Arc | BYPLM.A27R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | H | 11 | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 5
75 | BJBHT.A28R3 | BLECF_ | 448 | 0x | 01C0 | 6 | Arc | BYPLM.A28R3 | 3 | R |  |  |  | 6-7 | SR3 | BY05 | H | 12 | 6-7 | BY02 | R | 3 | 17 | 13 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary Romain and fiber connection 6-7 or 7-8 needs to be verified | bar: Modulation 6
76 | BJBHT.A29R3 | BLECF_ | 489 | 0x | 01E9 | 6 | Arc | BYPLM.A29R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 7 | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 4; Modulation 6
80 | BJBHT.A33R3 | BLECF_ | 453 | 0x | 01C5 | 6 | Arc | BYPLM.A33R3 | 3 | R |  |  |  | 7-8 | SR3 | BY05 | I | 11 | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1
81 | BJBHT.A34R3 | BLECF_ | 109 | 0x | 006D | 6 | Arc | BYPLM.A34R3 | 3 | R |  |  |  | 6-7 | SR3 | BY05 | I | 12 | 6-7 | BY02 | R | 3 | 20 | 16 | 1-8 |  | OK | ↑ | OK | ↑ | ↑ | [16 empty] | Romain & Ewald: LF in B fiber connection need to be checked
8 | BJBHT.A26L4 | BLECF_ | 318 | 0x | 013E | 6 | Arc | BYPLM.A26L4 | 4 | L |  |  |  | 7-8 | SX4 | BY05 | H | 4 | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 6
25 | BJBHT.B10L5 | BLECF_ | 14 | 0x | 000E | 6 | RR53 | BY02 | 5 | CL | 2 | 7 | B | 9-10 | SR5 | BY05 | C | 3 | 9-10 | BY02 | L | 1 | 7 | 4 | 1-8 |  | OK | OK | ↑ | OK | ↑ | [16 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 2
35 | BJBHT.C4L5 | BLECF_ | 356 | 0x | 0164 | 6 | RR53 | BY02 | 5 | CL | 1 | 7 | A | 13-14 | SR5 | BY05 | C | 2 | 1-2 | BY02 | L | 1 | 4 | 1 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 1
60 | BJBHT.B11R5 | BLECF_ | 603 | 0x | 025B | 6 | RR57 | BY02 | 5 | CR | 2 | 9 | B | 13-14 | SR5 | BY05 | C | 9 | 1-2 | BY02 | R | 3 | 7 | 4 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Slava: check of the database, if databse is o.k check in th tunnel by Ion | bar: Modulation 7 to Modulation 8
23 | UD62 | BLECF_ | 187 | 0x | 00BB | 8 | UJ63 | BY03 | 6 | CL | 3 | 1 | B | 17-18 | SR6 | BY05 | C | 4 | 5-6 | BY02 | C | 2 | 11 | 8 | 1-8 | Power loss could be checked | OK | OK | OK | OK | OK | [16 empty] | Ewald and Ion: Retesting of HV with Expert app. And evt. check in tunnel
51 | BJBHT.H4R6 | BLECF_ | 45 | 0x | 002D | 3 | UJ67 | BY03 | 6 | CR | 1 | 8 | A | 15-16 | SR6 | BY05 | C | 11 | 3-4 | BY02 | C | 2 | 16 | 12 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1
52 | BJBHT.DD | [5 empty] | UJ67 | BY03 | [39 empty] | Ewald and Ion: Testing of the LHCBLM-DD system
52 | BJBHT.DD | [5 empty] | UJ63 | BY03 | [39 empty] | Ewald and Ion: Testing of the LHCBLM-DD system
61 | BJBHT.A11R6 | BLECF_ | 72 | 0x | 0048 | 6 | UJ67 | BY03 | 6 | CR | 2 | 8 | B | 11-12 | SR6 | BY05 | C | 10 | 11-12 | BY02 | R | 3 | 6 | 3 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1 to Modulation 8
63 | TD68.2 | BLECF_ | 56 | 0x | 0038 | 8 | UJ67 | BY03 | 6 | CR | 2 | 10 | B | 15-16 | SR6 | BY05 | C | 9 | 3-4 | BY02 | C | 2 | 19 | 15 | 9-16 |  | OK | OK | ↑ | OK | ↑ | [16 empty] | Ewald and Romain: checking for GND Loop or bad connector | bar: LEVEL 8
64 | UD68 | BLECF_ | 82 | 0x | 0052 | 8 | UJ67 | BY03 | 6 | CR | 3 | 1 | B | 17-18 | SR6 | BY05 | C | 9 | 5-6 | BY02 | C | 2 | 20 | 16 | 1-8 |  | OK | OK | OK | OK | OK | [16 empty] | Ewald and Raymond: disconnecting broken SEM under the DUMP
30 | BJBHT.A8L8 | BLECF_ | 151 | 0x | 0097 | 6 | UA83 | BY05 | 8 | CL | 2 | 2 | B | 23-24 | SR8 | BY05 | C | 2 | 11-12 | BY02 | C | 2 | 7 | 4 | 9-16 |  | OK | OK | OK | OK | OK | [16 empty] | Jonathan and Ion: check in the tunnel necessary | bar: Modulation 1
46 | BJBHT.A4R8 | BLECF_ | 71 | 0x | 0047 | 7 | UA87 | BY06 | 8 | CR | 1 | 5 | B | 9-10 | SR8 | BY05 | C | 12 | 9-10 | BY02 | C | 2 | 15 | 11 | 1-8 | check in tunnel needed | OK | OK | OK | OK | OK | [16 empty] | Romain & Ewald: removing of the splitter (spare fibre)
Note on AQ5: effinger: Lower phase value -> Johnatan need s to check
Note on AG6: effinger: Cable repaired bt I,R and R (week 41)
Note on AT6: jemery: Database or connetion problem
Note on AO8: effinger: Lower phase value -> Johnatan need s to check
Note on AK10: effinger: Ch 5 goes every 20 seconds to 0 all the rest of the time it is working fine, even the runsum 11 is perfect at 1000 BLMbits
Note on AQ11: jemery: To high modulation signal
Note on AT11: jemery: One monitor missing out of 2!
Note on AQ12: jemery: Higher amplitude and smaller phase
Note on AS12: jemery: Higher amplitude and smaller phase
Note on AC13: effinger: LF fibre problem ! Is repaired
Note on AS13: jemery: Higher amplitude and smaller phase
Note on AP14: jemery: Higher amplitude and smaller phase
Note on AS15: jemery: Higher amplitude and smaller phase
Note on AA16: effinger: in the tunnel with TB o.k. --> Fibre broken tunnel to surface
Note on AB16: effinger: LF a&B fibre repaired
Note on AT16: jemery: Higher amplitude and smaller phase
Note on AR17: jemery: Higher amplitude and smaller phase
Note on AT17: jemery: Higher amplitude and smaller phase
Note on AO18: jemery: Higher amplitude and smaller phase
Note on AA19: effinger: in the tunnel with TB o.k. --> Fibre broken tunnel to surface
Note on AT21: jemery: Higher amplitude
Note on AP23: jemery: Lower phase
Note on AO24: jemery: Strange signal. Different amplitude and phase
Note on AU25: jemery: Missing expert name
Note on AV25: jemery: Expert name exist, but should be in ch 15
Note on AB27: effinger LF A&B 8.9.09 ! O.k 23.9.09
Note on AO28: jemery: Low amplitude
Note on AS31: jemery: Amplitude low phase higher
Note on AN32: effinger: CFC-ERROR
Note on AO35: jemery: Signal a bit low
Note on Z36: effinger: Splitter used!

## Sheet2
Tunnel - position
| HV box | CFC-Card |  | CFC - Position | [5 empty] | Patch |  | VME-TC position | [5 empty] | Comment
Pos. | position | No. |  | Place | Rack | P. | Pos. | Cr. | Slot |  | No. | Rack | VME | Crate | Slot | Card | Dec. |  | Comments | duration | priority
32 | BJBHT.A6L1 | BLECF_ | 638 | RR13 | BY02 | 1 | CL | 1 | 10 | A | 19-20 | BY02 | L | 1 | 5 | 2 | 1-8 |  | Jonathan and Ion: check in the tunnel necessary | 2h | 2
44 | BJBHT.A2R1 | BLECF_ | 501 | RR17 | BY02 | 1 | CR | 1 | 3 | A | 5-6 | BY02 | C | 2 | 14 | 10 | 1-8 |  | Slava: check of the database, if databse is o.k check in th tunnel by Ion | 1h | 2
45 | BJBHT.A3R1 | BLECF_ | 636 | RR17 | BY02 | 1 | CR | 1 | 4 | A | 7-8 | BY02 | C | 2 | 14 | 10 | 9-16 |  | Slava: check of the database, if databse is o.k check in th tunnel by Ion | 1h | 2
49 | BJBHT.A5R1 | BLECF_ | 437 | RR17 | BY02 | 1 | CR | 1 | 8 | A | 15-16 | BY02 | C | 2 | 16 | 12 | 1-8 |  | Jonathan and Ion: check in the tunnel necessary |  | 2
11 | BJBHT.A23L3 | BLECF_ | 730 | Arc | BYPLM.A23L3 | 3 | L |  |  |  | 7-8 | BY02 | L | 1 | 14 | 10 | 9-16 |  | Ewald and Romain: checking for GND Loop or bad connector | 2-4h | 1
31 | BJBHT.A7L3 | BLECF_ | 637 | UJ33 | BY02 | 3 | L | 1 | 10 | B | 19-20 | BY02 | C | 2 | 7 | 4 | 1-8 |  | Jonathan and Ion: check in the tunnel necessary (higher amp and 1 missing) | 0.5h | 1
67 | BJBHT.A20R3 | BLECF_ | 523 | Arc | BYPLM.A20R3 | 3 | R |  |  |  | 7-8 | BY02 | R | 3 | 13 | 9 | 1-8 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
68 | BJBHT.A21R3 | BLECF_ | 185 | Arc | BYPLM.A21R3 | 3 | R |  |  |  | 7-8 | BY02 | R | 3 | 13 | 9 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
71 | BJBHT.A24R3 | BLECF_ | 309 | Arc | BYPLM.A24R3 | 3 | R |  |  |  | 7-8 | BY02 | R | 3 | 15 | 11 | 1-8 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
74 | BJBHT.A27R3 | BLECF_ | 519 | Arc | BYPLM.A27R3 | 3 | R |  |  |  | 7-8 | BY02 | R | 3 | 16 | 12 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
75 | BJBHT.A28R3 | BLECF_ | 448 | Arc | BYPLM.A28R3 | 3 | R |  |  |  | 6-7 | BY02 | R | 3 | 17 | 13 | 1-8 |  | Jonathan and Ion: check in the tunnel necessary Romain and fiber connection 6-7 or 7-8 needs to be verified | 0.5h | 1
76 | BJBHT.A29R3 | BLECF_ | 489 | Arc | BYPLM.A29R3 | 3 | R |  |  |  | 7-8 | BY02 | R | 3 | 17 | 13 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
80 | BJBHT.A33R3 | BLECF_ | 453 | Arc | BYPLM.A33R3 | 3 | R |  |  |  | 7-8 | BY02 | R | 3 | 19 | 15 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
81 | BJBHT.A34R3 | BLECF_ | 109 | Arc | BYPLM.A34R3 | 3 | R |  |  |  | 6-7 | BY02 | R | 3 | 20 | 16 | 1-8 |  | Romain & Ewald: LF in B fiber connection need to be checked | 0.5h | 1
8 | BJBHT.A26L4 | BLECF_ | 318 | Arc | BYPLM.A26L4 | 4 | L |  |  |  | 7-8 | BY02 | L | 1 | 15 | 11 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 2
25 | BJBHT.B10L5 | BLECF_ | 14 | RR53 | BY02 | 5 | CL | 2 | 7 | B | 9-10 | BY02 | L | 1 | 7 | 4 | 1-8 |  | Slava: check of the database, if databse is o.k check in th tunnel by Ion | 0.5h | 2
35 | BJBHT.C4L5 | BLECF_ | 356 | RR53 | BY02 | 5 | CL | 1 | 7 | A | 13-14 | BY02 | L | 1 | 4 | 1 | 1-8 |  | Slava: check of the database, if databse is o.k check in th tunnel by Ion | 0.5h | 2
60 | BJBHT.B11R5 | BLECF_ | 603 | RR57 | BY02 | 5 | CR | 2 | 9 | B | 13-14 | BY02 | R | 3 | 7 | 4 | 9-16 |  | Slava: check of the database, if databse is o.k check in th tunnel by Ion | 0.5h | 2
23 | UD62 | BLECF_ | 187 | UJ63 | BY03 | 6 | CL | 3 | 1 | B | 17-18 | BY02 | C | 2 | 11 | 8 | 1-8 | Power loss could be checked | Ewald and Ion: Retesting of HV with Expert app. And evt. check in tunnel | 2h | 2
51 | BJBHT.H4R6 | BLECF_ | 45 | UJ67 | BY03 | 6 | CR | 1 | 8 | A | 15-16 | BY02 | C | 2 | 16 | 12 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 2
52 | BJBHT.DD |  |  | UJ67 | BY03 | [13 empty] | Ewald and Ion: Testing of the LHCBLM-DD system | 3-4h | 2
52 | BJBHT.DD |  |  | UJ63 | BY03 | [13 empty] | Ewald and Ion: Testing of the LHCBLM-DD system | 3-4h | 2
61 | BJBHT.A11R6 | BLECF_ | 72 | UJ67 | BY03 | 6 | CR | 2 | 8 | B | 11-12 | BY02 | R | 3 | 6 | 3 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5 | 2
63 | TD68.2 | BLECF_ | 56 | UJ67 | BY03 | 6 | CR | 2 | 10 | B | 15-16 | BY02 | C | 2 | 19 | 15 | 9-16 |  | Ewald and Romain: checking for GND Loop or bad connector | 2-4h | 2
64 | UD68 | BLECF_ | 82 | UJ67 | BY03 | 6 | CR | 3 | 1 | B | 17-18 | BY02 | C | 2 | 20 | 16 | 1-8 |  | Ewald and Raymond: disconnecting broken SEM under the DUMP | 0.5h | 2
31 | BJBHT.A7L7 | BLECF_ | 411 | RR73 | BY01 | 7 | CL | 2 | 10 | D | 15-16 | BY02 | E | 4 | 4 | 1 | 1-8 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
33 | BJBHT.H6L7 | BLECF_ | 118 | RR73 | BY01 | 7 | CL | 2 | 8 | D | 11-12 | BY02 | C | 2 | 11 | 8 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
76 | BJBHT.A10R7 | BLECF_ | 381 | RR77 | BY02 | 7 | CR | 3 | 6 | E | 3-4 | BY02 | R | 3 | 7 | 4 | 1-8 |  | Check in the tunnel if channel 7 and 8 are mix up | 0.5h | 1
30 | BJBHT.A8L8 | BLECF_ | 151 | UA83 | BY05 | 8 | CL | 2 | 2 | B | 23-24 | BY02 | C | 2 | 7 | 4 | 9-16 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
42 | BJBHT.A1R8 | BLECF_ | 78 | UA87 | BY06 | 8 | CR | 1 | 1 | B | 1-2 | BY02 | C | 2 | 13 | 9 | 1-8 |  | Jonathan and Ion: check in the tunnel necessary | 0.5h | 1
46 | BJBHT.A4R8 | BLECF_ | 71 | UA87 | BY06 | 8 | CR | 1 | 5 | B | 9-10 | BY02 | C | 2 | 15 | 11 | 1-8 | check in tunnel needed | Romain & Ewald: removing of the splitter (spare fibre) | 0.5h | 1
Note on S16: effinger: in the tunnel with TB o.k. --> Fibre broken tunnel to surface
Note on S19: effinger: in the tunnel with TB o.k. --> Fibre broken tunnel to surface
Note on R41: effinger: Splitter used!