## Slide 2: (Re-)validation tests of UPS powering post LS1 Acknowledgements: V.Chareyre, H.Thiesen, M.Zerlauth

## Slide 3: Motivation
Machine Protection Systems depend on UPS power to maintain protection and diagnostics function during power outages and perturbations
  UPS power was reconfigured after 2008 incident to guarantee truly redundant powering (F3/F4 lines in tunnel for e.g. QPS, additional power from other IP side in even points,…)
  Separation came with degradation of availability and maintainability
  LS1 campaign used by EN/EL to consolidate situation and restore dependable powering -> MPP presentation V.Chareyre May 2013
Changes require re-validation and allow for identification of potential errors/short-comings in design (QPS powering F3/F4, LBDS powering, BIS CIBUs…)

## Slide 4: Why to test redundant powering?
Verify that single protecting systems have redundant power supplies, i.e. they are supplied by true independent power distribution lines
Verify that redundant systems are powered from the correct power path
Verify that machine protection is still fully operational even if a complete distribution line is lost (although protected by UPS)
  Identify interdependencies between systems!
Verify that magnet powering is stopped in degraded powering conditions (as the PIC may not be triggered by the UPS systems!)
Verify the impact on other users (not having redundant systems nor redundant powering). They are or will be interested by this test!
Always mentioned but never done! -> Some incidents in run 1, following a lot of consolidation works during LS1, so it’s high time to do it!

## Slide 5: Overview of the UPS Network for the LHC
Example in one alcove (RE): 2 UPS parallel-redundant systems
Example in one even LHC point: 2 UPS parallel-redundant systems in UA (left), US and UA (right)
64 UPS systems for powering the LHC machine systems (RE alcoves, LHC even points (US and UA zones), LHC odd point)s
UPS network for all users requesting safe powering!
  QPS (quench protection systems)
  Beam interlock systems
  Beam Loss Monitors
  Cryo, Vac, WorldFip, Star-points
Backup time defined by the QPS systems: 10 min, strict minimum for continuing protecting the magnets after a fast power abort (energy extraction time constant)
Courtesy V.Chareyre

## Slide 6: New UPS Configuration in the alcoves and Odd Points
3rd UPS (UPS backup) powering the bypass of both UPS F3 and UPS F4 = Stand-by redundancy
‘Natural’ redundancy
No communication bus between the 3 UPS systems
Output UPS power protected
Distribution
Unchanged
Courtesy V.Chareyre

## Slide 7: UPS Configuration in UA and US zones
Output UPS power protected
UPS configuration not changed
UPS system replacement one-to-one
In case of failure of one UPS system in a redundant UPS configuration:
  Stop of the faulty UPS system
  Automatic transfer of the full load to the remaining UPS system
  F3 and F4 distribution lines fully protected
Courtesy V.Chareyre

## Slide 8
Résultats des tests HC-AUG
(2008-2009)
EN-EL, HCC Team et Hugues Thiesen

## Slide 9
Objective
  Annual AUG tests were used to verify that equipment powered with ‘secure’ power (UPS, Diesel,…) is behaving properly during power cuts
Systems concerned
  Safety systems
    ACESS,
    ODH et Fire detection,
    RadMon et Ramses
  Machine protection
    QPS, QHPS, 13kA-EE, 600A-EE
    PIC, WIC, BIC
    Power Converters
  Cryo
    Cryo
    Vide
  Beams
    RF,
    Beam Instrumentation,
    Beam Transfert and Beam Dump
  Infrastructure
    CV
    EL
    TI
    Star Point
Excluded systems
  Expériences
Courtesy H.Thiesen

## Slide 10
Sequence of tests
  AUG tests organised / point and concerned
    The point under test (surface and underground),
    The two adjacent sectors, roughly ½ arc on each side
  Interruption of normal AC supply until complete cut of network supplies
    After 10 minutes the UPS systems were stopped
  According to client system
    Non-secured network clients affected by initial cuts
    Systems powered by UPS affected by UPS cut
    Systems on secure network do not see any interruption
T
I
2
T
I
8
S
P
S
I
n
j
e
c
t
i
o
n
I
n
j
e
c
t
i
o
n
B
e
a
m
d
u
m
p
Point 5
Point 4
Point 2
Point 3
Point 6
Point 7
Point 1
Point 8
Courtesy H.Thiesen

## Slide 11
11
Test results
No major problem observed, however a number of small but important problems revealed
Machien Protection Systems
  QPS, QHPS, 13kAEE et 600A-EE
    Rack QPS of MQ.15R5 not on UPS
    4 cells in the arc23 (2R) found linked to mains instead to UPS
    Certain WorldFIP repeater not connected on UPS (lost comunication)
    …
  PIC, WIC et BIC
    Communication problem in point 5 (Star Point?),
    Inversion of UPS/AUG signals in point 1,
  Power Converters
    EIS convertes not on secure network => access problem after end of UPS autonomy
  Beam Instrumentation
    Pb with 3 crates BLM in SR2,
  Beam transfer (pts 2, 4, 6 et 8)
    Tests not significant as equipment condemnd…
Courtesy H.Thiesen

## Slide 12
Proposal for test procedure post LS1

## Slide 13: How to test redundant UPS powering
  The IT star-point rack (powered by the UPS F3) is transferred to a temporary power supply
  The switchboard (EOD F4) downstream the UPS F4 is switched off
  MP users verify that:
    Their equipment remain powered by the F3 distribution line
    And/or their redundant equipment A are still powered while equipment B are switched off
  Then the switchboard (EOD F4) is powered again
  The switchboard (EOD F3) downstream the UPS F3 is switched off
  MP users verify that:
    Their equipment remain powered by the F4 distribution line
    And/or their redundant equipment B are still powered while equipment A are switched off
  The other users (without redundant powering) can only see and note the impact!
  Optional in UA63/67: Cut 2nd time EOD F4 to verify LBDS functionality
  Then the switchboard (EOD F3) downstream the UPS F3 is powered again
  The IT star-point rack is transferred back to its initial power supply coming from the UPS F3
Notes:
‘Backup UPS’ in the alcoves and odd points
No operation on the UPS systems
PIC not triggered!

## Slide 14: What needs to be tested – REs / odd points
New configuration with 3 UPS systems and 2 redundant power paths F3/F4:
  Each RE alcove  x 16
  Each odd LHC point  x 4
  Each even LHC point -> x4
  Test procedure to be applied 24 times
  Tbd if surface UPS should be tested as well
Each RE covers ½ arc, impact from half-cell 11 up to 34
Each LHC odd point covers from half-cell 10L up to 10R
Each LHC even point covers from half-cell 10L up to 10R

## Slide 15: When to test?
Obviously when all systems are present and connected, but impact on operation systems (cryogenics, vacuum,..) is still minor
Proposal: After the already scheduled AUG tests (during initial cool-down of sectors)
For each RE alcove /LHC odd point: 1/2 day to perform the test
For each LHC even point: 1 day
Perform tests together
with planned AUG tests
before/early into cool-down

## Slide 16: UPS test planning in 2014
Tests to take place at end of AUG tests to profit from synergies
½ -1 day of additional test time / zone
Type Test Mid April: IR6 (LBDS dry-run?!)
End April: IR7
Early May: IR8
Mid June: IR1
End June: IR2 & IR3
End July: IR4 & IR5
Organistion: I.Romera (MPE), H.Thiesen (EPC), V.Chareyre (EL), M.Solfaroli & M.Pojer (HWC)

## Slide 17: Conclusion
  Revalidation strongly recommended following consolidation and run 1 experience -> Should also surface UPS be considered?
  No major problems expected, will however reveal numerous small but important non-conformities which require correction before restarting the machine
  Use synergies with (already scheduled) AUG tests to minimize impact
    Requires additional ½ day for odd points and 1 day for even points (conservative)
    Only clients on UPS networks affected, normal network will remain powered
  Due to ‘early’ timing tests might however not be fully significant for some equipment types (equipment condemned during shut-down,…)
  Next steps
    Finalize survey for impact/requirements from all relevant users
    Integration into in official LHC planning (following presentation in LSC before end of the year)
    Prepare and circulate procedure describing test and required preparation (early 2014)

## Slide 18
End

## Slide 19: Questions to client systems
Do you have any concerns for the safety/availability of your equipment during the tests (Cryo, Vac)
Will the test at proposed time allow to validate redundant powering, i.e. will remote diagnostic be available?
Do you have any additional request wrt to ‘standard procedure’ (cut sequentially F3/F4)
Do you have any additional request for network configuration prior to test (e.g. powering of diagnostic racks,..)?
Do you have any equipment in the LHC surface buildings racks?!
Pleas name a contact person representing your team during the test